## 하중계산
Code | ASCE 7-02 Minimum Design Loads for Buildings and Other Structures, Chpater 6, Wind Loads
| Main Wind-Force Resisting System | (MWFRS)
| 송전탑 높이 (h, m) | 59.135
| low-rise or open | open |  | open area가 gross area의 80%를 넘음
| Flexible or rigid | flexible
입력해야하는 값
계산에 사용되지 않음
번호 | 항목 | 값 | 참조 | 근거
1 | Basic wind speed (V, m/s) | 43 | Fig. 6-1 | 1971년부터 2014년까지 한국에 기록된 최대풍속(2007년 9월 16일 고산 NNW) | http://www.kma.go.kr/
2 | Wind Directionality Factor(Kd) | 0.85 | Table 6-4 | Lattice Framework
3 | Building and Structure Category | IV | Table 1-1 | Ancillary structures(tower)
4 | Importance Factor (I) | 1.15 | Table 6-1 | Building and Structure Category(3번항목)가 IV이므로
5 | Surface Roughness | B | 6.5.6.2 | suburban areas, wooded areas
6 | Exposure Categories | B | 6.5.6.3 | Surface Roughness(5번항목)가 B이므로
7 | Topographic Factor (Kzt) | 1 | 6.5.7 | 편의상 평지를 가정(6.5.7.1의 모든 조건 불만족)
8 | Gust Effect Factor (Gf) | 0.51319 | 6.5.8.1 | Felxible이므로 식 (6-8)이용
| Building natural frequency (n1, Hz) | 1
| peak factor for background resonant response (gQ) | 3.4 | 6.5.8.1 | 식 (6-6)에서 지정됨
| peak factor for wind response (gv) | 3.4 | 6.5.8.1 | 식 (6-6)에서 지정됨
| peak factor for resonant response (gR) | 4.1895 | 6.5.8.2 | 식 (6-9)
| mean hourly wind-speed power law exponent (alpha_bar) | 0.25 | Table 6-2 | 식 (6-14)
| mean hourly wind speed factor (b_bar) | 0.45 | Table 6-2
| equivalent height of structure (z_bar) | 35.481 | 6.5.8.1 | 0.6*h (Table 6-2로부터 9.14보다 낮을땐 9.14 이용)
| mean houlry wind speed at height z_bar (Vz_bar, m/s) | 4.5838 | 6.5.8.2 | 식 (6-14)
| 바람방향에 수직인 길이 (B,m) | 26961 |  | 사영면적이 가장 큰 방향을 수직으로 가정
| 바람방향에 평행한 길이 (L,m) | 7230 |  | 사영면적이 가장 큰 방향을 수직으로 가정(top,mid,bot의 평균)
| eta for Rh | 59.3436 | 6.5.8.2
| eta for RB | 27056.1138 | 6.5.8.2 | E는 생략
| eta for RL | 24290.1729 | 6.5.8.2
| Rh | 0.016709 | 6.5.8.2 | eta가 양수면 1이고 아니면 식 (6-13a)를 따름
| RB | 3.696e-05 | 6.5.8.2 | eta가 양수면 1이고 아니면 식 (6-13a)를 따름
| RL | 4.1168e-05 | 6.5.8.2 | eta가 양수면 1이고 아니면 식 (6-13a)를 따름
| l | 97.54 | Table 6-2
| epsilon_bar | 0.33333 | Table 6-2
| integral length scale of turbulence (Lz_bar) | 148.7698 | 6.5.8.1 | 식 (6-7)
| reduced frequency (N1) | 32.4553 |  | 식 (6-12)
| Rn | 0.014982 |  | 식 (6-11)
| damping ratio, percent of critical (beta) | 1
| resonant response factor (R) | 7.0028e-05 |  | 식 (6-14)
| turbulence intensity factor (c) | 0.3 | Table 6-2
| intensity of turbulence (Iz_bar) | 0.24292 | 6.5.8.1 | 식 (6-5)
| background response factor (Q) | 0.23772 | 6.5.8.1 | 식 (6-6)
9 | Velocity Pressure (qz, Pa) | 634.491 |  | 식 (6-15)
| 3-s gust-speed power law exponent (alpha) | 7 | Table 6-2 | Exposure category B
| nominal height of the atmospheric boundary layer (zg) | 1200 | Table 6-2 | Exposure category B
| height above ground level (z, ft) | 14.7638 | 단위=m | 4.5
| velocity pressure exposure coefficient (Kz) | 0.57472 | Table 6-3 | z<15 ft (15ft=4.572m)
|  | 0.57212 | Table 6-3 | 15ft<z<zg, 모든 요소가 이 구간에 있음을 가정
10 | Internal pressure coefficient (Gcpi) | 0 | Fig. 6-5 | for open building
11 | Reduction Factor (Ri) | 1 | 6.5.11.1 | 식 (6-16), Gcpi가 어짜피 0이므로 무관
12 | Force Coefficients (Cf) | 2 | Fig. 6-22 | epsilon(ratio of solid area to gross area)이 0.1보다 작고 Flat-sided member
13 | Design wind loads (F, N) | 651.228 | 6.5.15 | 식 (6-28)
| projected area (Af) | 1 | sheet3 | 해당 요소의 면적을 입력

## 풍속(기상청)
지점 |  | 2011년 |  |  |  | 2012년 |  |  |  | 2013년 |  |  |  | 2014년
번호 | 지명 | 값 | 풍향 | 월 | 일 | 값 | 풍향 | 월 | 일 | 값 | 풍향 | 월 | 일 | 값 | 풍향 | 월 | 일
90 | 속초 | 11.8 | WNW | 5 | 13 | 14.6 | SE | 8 | 28 | 11.1 | W | 11 | 18 | 11.9 | W | 5 | 3
95 | 철원 | 9.2 | SW | 4 | 24 | 10.7 | NE | 9 | 17 | 10.3 | SSW | 11 | 25 | 9.8 | WSW | 5 | 2
98 | 동두천 | 9.9 | WNW | 3 | 15 | 12.6 | SE | 8 | 28 | 11.1 | WSW | 11 | 25 | 11.7 | WNW | 12 | 1
99 | 파주 | 8.5 | WSW | 4 | 24 | 8.9 | WNW | 4 | 3 | 10.8 | S | 11 | 25 | 9.2 | NW | 12 | 1
100 | 대관령 | 15 | W | 1 | 8 | 17.8 | W | 11 | 11 | 16.7 | W | 11 | 25 | 17.9 | WSW | 7 | 26
101 | 춘천 | 7.4 | WSW | 5 | 13 | 8.8 | WSW | 4 | 6 | 7.6 | SSE | 5 | 12 | 8.3 | NW | 3 | 20
102 | 백령도 | 21.6 | SW | 8 | 8 | 21.5 | WNW | 8 | 28 | 24.9 | SNS | 11 | 25 | 19.1 | ESE | 5 | 11
104 | 북강릉 | 12 | SW | 5 | 13 | 11.6 | W | 12 | 4 | 11.4 | WSW | 11 | 25 | 11.2 | WNW | 5 | 3
105 | 강릉 | 11.4 | W | 5 | 13 | 10.8 | W | 11 | 12 | 14.3 | SNS | 11 | 25 | 11.6 | NW | 5 | 13
106 | 동해 | 11.1 | NNW | 4 | 15 | 14.6 | NNW | 9 | 17 | 16.2 | WSW | 11 | 25 | 14.8 | NNE | 10 | 13
108 | 서울 | 10.9 | ENE | 6 | 26 | 13.7 | SSW | 8 | 28 | 12.6 | SW | 11 | 25 | 11.1 | WNW | 12 | 1
112 | 인천 | 12.8 | NNW | 12 | 22 | 16.1 | NNW | 4 | 3 | 14.2 | W | 11 | 25 | 14.9 | NNW | 12 | 1
114 | 원주 | 8.2 | WNW | 1 | 15 | 9.3 | S | 8 | 28 | 8.1 | WSW | 4 | 9 | 8.1 | WNW | 12 | 1
115 | 울릉도 | 21.6 | ENE | 4 | 19 | 17.5 | SW | 7 | 6 | 17.8 | NE | 4 | 7 | 16.1 | NE | 4 | 4
119 | 수원 | 9.9 | E | 6 | 26 | 14.1 | E | 8 | 28 | 8.6 | W | 4 | 9 | 9.7 | SSW | 7 | 26
121 | 영월 | 7.8 | N | 8 | 8 | 9.3 | SSE | 8 | 28 | 9.9 | SE | 4 | 17 | 10.9 | WNW | 12 | 1
127 | 충주 | 8.8 | W | 1 | 15 | 9.6 | W | 4 | 6 | 9 | - | 4 | 9 | 8.9 | SW | 7 | 26
129 | 서산 | 15 | S | 8 | 8 | 16.2 | WNW | 4 | 3 | 10 | W | 4 | 9 | 10.4 | WNW | 3 | 20
130 | 울진 | 16.1 | NW | 4 | 16 | 18.4 | NW | 9 | 17 | 12.4 | NW | 3 | 10 | 11.4 | WNW | 12 | 1
131 | 청주 | 6.3 | ENE | 9 | 3 | 10.3 | SE | 8 | 28 | 6.7 | NNE | 8 | 6 | 6.9 | NE | 10 | 13
133 | 대전 | 10.5 | ESE | 8 | 7 | 13.9 | SSE | 8 | 28 | 8.4 | SSW | 4 | 16 | 10.1 | S | 5 | 7
135 | 추풍령 | 11.6 | WSW | 5 | 1 | 14.5 | W | 4 | 3 | 11.4 | W | 1 | 3 | 10.9 | W | 12 | 1
136 | 안동 | 9.2 | WNW | 1 | 15 | 10.3 | WNW | 4 | 6 | 10 | SNS | 8 | 6 | 9.1 | WNW | 11 | 12
137 | 상주 | 11.1 | WNW | 1 | 15 | 11.9 | WNW | 4 | 6 | 9.5 | SNS | 3 | 20 | 11.4 | W | 12 | 1
138 | 포항 | 9.4 | SW | 6 | 23 | 12.7 | S | 9 | 17 | 11 | NNE | 10 | 8 | 10.5 | NNE | 10 | 13
140 | 군산 | 13.5 | SW | 4 | 30 | 18.8 | NW | 4 | 3 | 13 | W | 12 | 11 | 13.9 | WSW | 12 | 1
143 | 대구 | 8.5 | W | 1 | 29 | 10 | W | 4 | 3 | 8.6 | W | 4 | 9 | 9.2 | WNW | 12 | 1
146 | 전주 | 9.6 | SE | 5 | 6 | 16.3 | SE | 8 | 28 | 10.6 | SE | 11 | 24 | 8.5 | SE | 5 | 11
152 | 울산 | 11.6 | NE | 7 | 19 | 13 | WSW | 4 | 3 | 10.4 | SNS | 4 | 14 | 11.6 | ESE | 8 | 3
155 | 창원 | 9.9 | WSW | 8 | 8 | 18.2 | SE | 9 | 17 | 8 | S | 3 | 18 | 16.3 | ESE | 8 | 2
156 | 광주 | 14 | SSW | 4 | 30 | 14.6 | SSE | 8 | 28 | 10.5 | SSW | 7 | 16 | 9.4 | SW | 7 | 26
159 | 부산 | 14.5 | SW | 4 | 8 | 17.8 | SSE | 9 | 17 | 15.8 | SW | 3 | 13 | 14.6 | SW | 3 | 18
162 | 통영 | 14.7 | SSE | 8 | 8 | 25.5 | SE | 9 | 17 | 16.9 | SE | 2 | 1 | 15.1 | SSE | 5 | 12
165 | 목포 | 16.6 | S | 8 | 7 | 24.2 | N | 8 | 30 | 14.8 | N | 3 | 20 | 14.8 | N | 2 | 3
168 | 여수 | 19.6 | SSW | 8 | 8 | 27.7 | ENE | 9 | 17 | 18 | SW | 11 | 25 | 18.4 | SW | 8 | 25
169 | 흑산도 | 29.1 | SSE | 8 | 7 | 35.1 | SE | 8 | 28 | 19.2 | SSE | 11 | 24 | 26.4 | SSE | 6 | 2
170 | 완도 | 18.1 | SE | 8 | 7 | 36.3 | SSE | 8 | 28 | 13.6 | NW | 12 | 20 | 20.3 | ESE | 8 | 2
172 | 고창 | 17.8 | E | 8 | 7 | 22.2 | SE | 8 | 28 | 17.2 | SE | 11 | 24 | 16.5 | ESE | 8 | 2
174 | 순천 | 13.2 | SE | 8 | 7 | 17.2 | SE | 8 | 28 | 9.4 | SNS | 4 | 9 | 10.6 | SE | 8 | 2
175 | 진도 | 26.1 | SSE | 8 | 7 | 33.6 | SSE | 8 | 28 | 16.3 | NNW | 3 | 10 | 20.5 | ESE | 8 | 2
184 | 제주 | 16.5 | S | 4 | 30 | 18.2 | SSW | 8 | 28 | 16 | NNE | 10 | 8 | 14.6 | NW | 12 | 16
185 | 고산 | 28 | SE | 8 | 7 | 29.9 | SE | 8 | 28 | 25.3 | WSW | 11 | 27 | 26.8 | NW | 12 | 17
188 | 성산 | 18.3 | ESE | 8 | 7 | 25 | SE | 8 | 27 | 15 | N | 10 | 8 | 17.2 | E | 8 | 2
189 | 서귀포 | 16.4 | SSE | 8 | 7 | 19 | SE | 8 | 28 | 10.5 | SSW | 11 | 24 | 10.7 | NE | 10 | 13
192 | 진주 | 7.9 | SE | 8 | 7 | 9.5 | ESE | 8 | 28 | 7.6 | WSW | 11 | 25 | 8.2 | W | 12 | 1
201 | 강화 | 9.9 | SW | 7 | 27 | 14.7 | SW | 8 | 28 | 13.6 | SW | 11 | 25 | 10.6 | SSW | 7 | 26
202 | 양평 | 7.6 | WSW | 5 | 13 | 10.9 | SE | 8 | 28 | 9.7 | WSW | 4 | 9 | 8.5 | WNW | 12 | 1
203 | 이천 | 7.9 | SW | 5 | 9 | 10.5 | S | 8 | 28 | 7.3 | W | 4 | 9 | 7.6 | SSW | 7 | 26
211 | 인제 | 8.1 | S | 5 | 13 | 8.1 | S | 8 | 29 | 8.7 | S | 11 | 25 | 7.4 | S | 7 | 26
212 | 홍천 | 7.1 | W | 4 | 25 | 7.8 | W | 4 | 5 | 6.9 | WSW | 4 | 29 | 7.7 | W | 5 | 4
216 | 태백 | 9.5 | WSW | 4 | 30 | 9.8 | WSW | 10 | 22 | 8.1 | SW | 4 | 29 | 9.3 | SW | 7 | 26
217 | 정선군 | 14.8 | NNE | 1 | 15 | 15.6 | NNE | 11 | 13 | 17.2 | NNE | 4 | 16 | 14.7 | NNE | 7 | 26
221 | 제천 | 9.4 | WNW | 5 | 13 | 9.2 | W | 4 | 6 | 9.8 | WSW | 4 | 9 | 8.2 | W | 12 | 1
226 | 보은 | 8.3 | NNW | 3 | 15 | 9.6 | NW | 4 | 6 | 8.5 | SNS | 4 | 9 | 8.8 | NW | 12 | 1
232 | 천안 | 10.9 | W | 3 | 15 | 13.9 | E | 8 | 28 | 10.7 | W | 4 | 9 | 9.9 | WNW | 12 | 1
235 | 보령 | 14.4 | S | 4 | 30 | 17.5 | S | 8 | 28 | 12.7 | SSW | 8 | 29 | 13.6 | S | 7 | 26
236 | 부여 | 8.9 | SE | 8 | 8 | 14.7 | SE | 8 | 28 | 9.1 | W | 4 | 9 | 8.8 | SSW | 7 | 26
238 | 금산 | 8.3 | S | 8 | 8 | 9.5 | S | 8 | 28 | 8 | SW | 4 | 14 | 8 | N | 3 | 7
243 | 부안 | 12.9 | SSW | 4 | 30 | 15.9 | SSE | 8 | 28 | 11.3 | SSW | 4 | 16 | 9.8 | S | 3 | 17
244 | 임실 | 9.5 | SSW | 4 | 30 | 12.9 | S | 8 | 28 | 10.1 | SW | 4 | 16 | 8.4 | W | 3 | 20
245 | 정읍 | 7.4 | W | 10 | 15 | 9.3 | ESE | 8 | 28 | 7.2 | WSW | 11 | 27 | 7.3 | W | 12 | 1
247 | 남원 | 10.2 | SSE | 8 | 7 | 13.9 | SSE | 8 | 28 | 9.2 | SNS | 4 | 9 | 9.8 | ENE | 4 | 28
248 | 장수 | 9.3 | W | 3 | 15 | 10.9 | E | 4 | 3 | 9.6 | W | 3 | 10 | 9.3 | SSE | 6 | 2
251 | 고창군 | 10.5 | SSE | 4 | 30 | 13.8 | SE | 8 | 28 | 11.8 | SE | 11 | 24 | 10 | ESE | 5 | 11
252 | 영광군 | 14.5 | S | 8 | 8 | 17.7 | SSE | 8 | 28 | 11.6 | NW | 12 | 20 | 12.2 | SE | 6 | 2
253 | 김해시 | 13 | SE | 8 | 8 | 19.9 | SE | 9 | 17 | 11.4 | S | 11 | 25 | 12.2 | ESE | 8 | 3
254 | 순창군 | 11.6 | W | 3 | 24 | 16.1 | SE | 8 | 28 | 12.1 | W | 4 | 11 | 10.7 | NNW | 3 | 20
255 | 북창원 | 8 | NNE | 7 | 19 | 10.8 | ESE | 8 | 28 | 8.4 | N | 10 | 8 | 8 | ESE | 8 | 2
257 | 양산시 | 9.6 | ENE | 9 | 3 | 12.8 | WSW | 4 | 3 | 10.7 | WSW | 3 | 18 | 9.8 | W | 12 | 1
258 | 보성군 | 17 | ESE | 8 | 7 | 24.4 | ESE | 8 | 28 | 13 | SNS | 4 | 6 | 15.1 | WNW | 12 | 1
259 | 강진군 | 20.8 | SE | 8 | 7 | 25.2 | SE | 8 | 28 | 12.2 | SE | 5 | 27 | 17.9 | E | 8 | 2
260 | 장흥 | 15.5 | SSE | 8 | 7 | 20.3 | SE | 8 | 28 | 10.7 | NNE | 3 | 1 | 14 | SSE | 8 | 2
261 | 해남 | 14.3 | NNE | 8 | 7 | 18.6 | ESE | 8 | 28 | 8.3 | SE | 5 | 27 | 14.1 | E | 8 | 2
262 | 고흥 | 12.3 | S | 8 | 7 | 15.4 | S | 8 | 28 | 10 | NW | 3 | 1 | 10.5 | NW | 4 | 5
263 | 의령군 | 11.3 | W | 5 | 1 | 15.5 | E | 4 | 3 | 11.5 | ESE | 4 | 9 | 13.3 | WSW | 11 | 12
264 | 함양군 | 8.9 | WSW | 5 | 1 | 14 | WSW | 4 | 3 | 10.4 | WSW | 11 | 25 | 9.6 | W | 12 | 1
266 | 광양시 | 12.6 | NE | 7 | 19 | 15.5 | NNE | 9 | 17 | 11.6 | NE | 4 | 6 | 11.9 | W | 12 | 1
271 | 봉화 | 9.1 | NNW | 1 | 15 | 11.5 | N | 9 | 17 | 8 | NW | 1 | 25 | 9.3 | N | 10 | 13
272 | 영주 | 12.1 | NW | 1 | 29 | 12.4 | NW | 4 | 3 | 12.1 | NW | 3 | 20 | 12.3 | NW | 12 | 17
273 | 문경 | 8.6 | NW | 1 | 16 | 9.4 | WNW | 4 | 3 | 8.2 | W | 4 | 9 | 9.6 | NW | 4 | 3
276 | 청송군 | 11.2 | NNE | 1 | 15 | 10.7 | WSW | 4 | 3 | 13.5 | W | 8 | 10 | 9.8 | WSW | 11 | 12
277 | 영덕 | 14.7 | NNE | 9 | 3 | 16.4 | NNE | 9 | 17 | 14.6 | NNE | 10 | 8 | 14.1 | NNE | 10 | 13
278 | 의성 | 9.2 | NW | 1 | 15 | 9 | WNW | 4 | 6 | 8.4 | SNS | 8 | 10 | 8.8 | WNW | 12 | 17
279 | 구미 | 8.1 | WNW | 3 | 25 | 10.1 | W | 4 | 3 | 8.2 | SNS | 3 | 1 | 8.5 | WNW | 12 | 1
281 | 영천 | 8.8 | WNW | 3 | 15 | 10.1 | WNW | 4 | 3 | 9.4 | SNS | 3 | 1 | 9.6 | W | 12 | 17
283 | 경주시 | 10.8 | WNW | 3 | 30 | 13.2 | W | 4 | 3 | 12.8 | WSW | 4 | 16 | 11.6 | N | 5 | 28
284 | 거창 | 10.4 | SE | 8 | 8 | 15.7 | S | 8 | 28 | 9.6 | NW | 12 | 20 | 9.5 | NW | 12 | 17
285 | 합천 | 8.4 | NNE | 4 | 19 | 12.8 | NE | 9 | 17 | 8 | NNE | 9 | 22 | 7.2 | NNE | 10 | 13
288 | 밀양 | 8.6 | WNW | 5 | 1 | 12.1 | SSE | 9 | 17 | 8.4 | NNW | 8 | 4 | 10.1 | WNW | 12 | 1
289 | 산청 | 10.2 | WNW | 1 | 15 | 15.6 | W | 4 | 3 | 11.3 | W | 12 | 20 | 11.3 | WNW | 12 | 1
294 | 거제 | 9.1 | ESE | 8 | 8 | 13.3 | SE | 9 | 17 | 8.6 | NNW | 6 | 18 | 8.4 | ESE | 7 | 25
295 | 남해 | 8.4 | ESE | 8 | 7 | 9.2 | ENE | 9 | 17 | 6.4 | SSW | 3 | 9 | 6.4 | NW | 3 | 20
지점 번호: 지점; 2011년 값: 2006년; 2012년 값: 2007년; 2013년 값: 2008년; 2014년 값: 2009년 | 2010년
번호 | 지명 | 값 | 풍향 | 월 | 일 | 값 | 풍향 | 월 | 일 | 값 | 풍향 | 월 | 일 | 값 | 풍향 | 월 | 일 | 값 | 풍향 | 월 | 일
90 | 속초 | 30.5 | NNW | 10 | 23 | 14 | W | 3 | 27 | 12.2 | WNW | 2 | 22 | 12.6 | N | 3 | 19 | 11.9 | WNW | 4 | 13
95 | 철원 | 11.1 | NE | 8 | 19 | 11.2 | SW | 3 | 5 | 9.3 | SW | 5 | 6 | 12.5 | NNE | 4 | 27 | 12.8 | SW | 8 | 14
98 | 동두천 | 10 | SW | 3 | 4 | 10.2 | WSW | 5 | 12 | 9.3 | SSW | 4 | 25 | 10.6 | W | 12 | 5 | 10.2 | SSE | 9 | 2
99 | 문산 | 9.5 | NNE | 10 | 23 | 10.8 | NNW | 7 | 29 | 9.4 | SW | 4 | 25 | 8.6 | N | 4 | 28 | 8.2 | ENE | 9 | 2
100 | 대관령 | 17.8 | WSW | 2 | 9 | 20.7 | W | 3 | 5 | 15.5 | W | 5 | 6 | 16.9 | W | 12 | 5 | 18.1 | W | 9 | 2
101 | 춘천 | 8.4 | WSW | 4 | 19 | 8.9 | NW | 3 | 28 | 8.1 | WNW | 12 | 5 | 7.7 | NNW | 4 | 28 | 8.7 | SSE | 9 | 2
102 | 백령도 | 25.6 | W | 4 | 20 | 25.9 | W | 3 | 5 | 18.5 | SSE | 6 | 18 | 20.9 | SSW | 7 | 14 | 19.9 | SSW | 8 | 14
104 | 북강릉 | [8 empty] | 10.6 | SW | 12 | 5 | 12.5 | SW | 12 | 5 | 11 | SSW | 3 | 12
105 | 강릉 | 16 | NNW | 10 | 23 | 14.9 | WSW | 2 | 3 | 12.9 | SW | 5 | 6 | 13.2 | WSW | 12 | 5 | 14.9 | SW | 3 | 12
106 | 동해 | 15.7 | N | 10 | 23 | 15.4 | W | 2 | 3 | 13 | NNE | 3 | 19 | 13.2 | NNE | 10 | 8 | 14.9 | SW | 3 | 12
108 | 서울 | 10.9 | SW | 3 | 4 | 10 | SW | 3 | 5 | 10.9 | SW | 4 | 25 | 11.9 | SSW | 2 | 13 | 14 | SSW | 9 | 2
112 | 인천 | 12.9 | NNW | 4 | 20 | 13.9 | NNW | 1 | 6 | 14.4 | NNW | 11 | 29 | 14.6 | NW | 12 | 5 | 17.5 | S | 9 | 2
114 | 원주 | 7.9 | W | 4 | 23 | 8.1 | WSW | 3 | 11 | 7.8 | NE | 3 | 19 | 7.2 | NE | 11 | 11 | 7.8 | SSE | 9 | 2
115 | 울릉도 | 24.9 | NE | 9 | 18 | 27.1 | NNE | 9 | 17 | 17.6 | SSW | 5 | 6 | 17.4 | NE | 11 | 11 | 16.9 | WSW | 8 | 15
119 | 수원 | 10.2 | SSW | 3 | 4 | 10 | W | 1 | 6 | 8.5 | NW | 11 | 29 | 8.7 | ESE | 4 | 20 | 15.9 | SSE | 9 | 2
121 | 영월 | 11.1 | E | 6 | 10 | 11.4 | NW | 3 | 28 | 10.1 | WNW | 12 | 5 | 7.3 | NNW | 6 | 2 | 8 | ESE | 6 | 15
127 | 충주 | 10.1 | E | 5 | 2 | 10.6 | W | 3 | 28 | 9.3 | ESE | 5 | 12 | 8 | WSW | 12 | 5 | 8.4 | WSW | 4 | 27
129 | 서산 | 13.3 | WNW | 4 | 20 | 14.5 | SSW | 3 | 28 | 12.7 | W | 4 | 25 | 14.6 | SW | 7 | 9 | 27.3 | SE | 9 | 2
130 | 울진 | 24.2 | ESE | 7 | 10 | 14.4 | W | 1 | 6 | 13.2 | W | 12 | 5 | 15.3 | W | 2 | 20 | 13.5 | SW | 3 | 21
131 | 청주 | 7.2 | ENE | 7 | 10 | 7.9 | W | 5 | 14 | 6.7 | E | 4 | 20 | 6.8 | SSE | 6 | 30 | 6.7 | SE | 9 | 2
133 | 대전 | 8.3 | E | 7 | 10 | 8.8 | SSE | 5 | 18 | 9.4 | ESE | 4 | 9 | 8.2 | S | 7 | 14 | 10 | SSE | 9 | 2
135 | 추풍령 | 10.9 | W | 4 | 20 | 11.5 | W | 3 | 5 | 11.3 | W | 12 | 25 | 13.4 | W | 12 | 5 | 13.1 | WSW | 12 | 3
136 | 안동 | 10.1 | ESE | 7 | 10 | 13.4 | WNW | 3 | 28 | 7.8 | WNW | 11 | 29 | 8 | W | 12 | 5 | 9.4 | WNW | 12 | 3
137 | 상주 | 13 | W | 3 | 12 | 13.9 | WSW | 3 | 28 | 11 | W | 12 | 25 | 10.5 | W | 3 | 6 | 11.2 | W | 3 | 16
138 | 포항 | 10.8 | NNW | 9 | 17 | 11.2 | SSE | 8 | 12 | 8.4 | SSE | 5 | 18 | 11.7 | NE | 1 | 30 | 9.5 | WSW | 12 | 3
140 | 군산 | 16.4 | NNW | 11 | 6 | 16.7 | NNW | 1 | 7 | 15.7 | NNW | 11 | 29 | 15.3 | N | 12 | 5 | 15 | N | 12 | 8
143 | 대구 | 13.3 | WNW | 4 | 19 | 10.4 | WNW | 1 | 7 | 8.7 | E | 5 | 9 | 9 | W | 4 | 22 | 8.6 | WNW | 4 | 13
146 | 전주 | 10.5 | SSW | 8 | 4 | 10.5 | SSE | 3 | 4 | 9.3 | NW | 6 | 8 | 9.3 | SE | 4 | 20 | 10.4 | W | 3 | 20
152 | 울산 | 11.7 | ESE | 7 | 10 | 10.7 | SW | 4 | 20 | 11 | NW | 2 | 23 | 10.4 | W | 12 | 30 | 12.4 | SSW | 3 | 12
155 | 창원 | 20.3 | E | 7 | 10 | 18.4 | E | 9 | 16 | 10.2 | S | 5 | 18 | 11.2 | S | 2 | 13 | 12.4 | SE | 8 | 11
156 | 광주 | 12 | NE | 7 | 10 | 11.2 | NE | 7 | 14 | 11.1 | SW | 6 | 18 | 14.2 | SW | 2 | 13 | 12.2 | SW | 3 | 12
159 | 부산 | 16.7 | NNE | 9 | 17 | 15.6 | S | 3 | 4 | 12.7 | SSW | 5 | 18 | 18.3 | SW | 2 | 13 | 15.6 | SW | 11 | 11
162 | 통영 | 19.2 | S | 7 | 10 | 18.1 | S | 3 | 4 | 13.1 | S | 6 | 18 | 15.7 | S | 3 | 21 | 18.2 | SSE | 8 | 11
165 | 목포 | 17 | WSW | 2 | 7 | 16.6 | NW | 3 | 5 | 15 | N | 2 | 23 | 15 | N | 11 | 2 | 16.7 | N | 10 | 26
168 | 여수 | 26.7 | SW | 7 | 10 | 26.4 | ENE | 9 | 16 | 18.8 | NW | 12 | 5 | 22.3 | SSW | 2 | 13 | 19.9 | SSW | 2 | 25
169 | 흑산도 | 22.6 | N | 7 | 10 | 25.1 | SSE | 8 | 12 | 18.9 | NNW | 12 | 21 | 20.7 | SSE | 4 | 20 | 35.5 | SSE | 9 | 1
170 | 완도 | 28.6 | E | 7 | 10 | 26.4 | NNW | 9 | 16 | 17.8 | NNW | 2 | 23 | 16.4 | NW | 11 | 2 | 18.3 | NW | 1 | 21
172 | 고창 | [16 empty] | 15.3 | W | 12 | 28
175 | 진도 | 22.8 | ESE | 7 | 10 | 23.5 | SE | 8 | 12 | 19.8 | SE | 4 | 9 | 18 | SSE | 4 | 20 | 17.7 | S | 9 | 1
184 | 제주 | 15.1 | SW | 7 | 10 | 24.8 | NE | 9 | 16 | 12.7 | NW | 12 | 5 | 15.7 | SSW | 2 | 13 | 14.3 | NW | 1 | 13
185 | 고산 | 31.3 | NW | 2 | 7 | 43 | NNW | 9 | 16 | 27.6 | NNW | 12 | 5 | 27 | NW | 11 | 2 | 29.1 | WNW | 12 | 30
188 | 성산 | 19.9 | S | 7 | 10 | 25.9 | ENE | 9 | 16 | 12.9 | WNW | 12 | 5 | 15.7 | WNW | 3 | 22 | 14.8 | S | 8 | 11
189 | 서귀포 | 16.5 | SW | 7 | 10 | 16.7 | ESE | 9 | 16 | 9.9 | NE | 5 | 10 | 10.8 | S | 5 | 21 | 14.7 | SE | 8 | 10
192 | 진주 | 12.9 | WSW | 4 | 20 | 11.4 | W | 3 | 5 | 9.4 | WSW | 4 | 26 | 8.1 | WSW | 4 | 21 | 9.8 | WSW | 5 | 24
201 | 강화 | 8.8 | SW | 11 | 8 | 9.6 | SW | 3 | 10 | 11.6 | SW | 4 | 25 | 11.4 | SSW | 2 | 13 | 11 | SW | 12 | 10
202 | 양평 | 7.3 | WSW | 4 | 19 | 8.3 | WSW | 3 | 5 | 7.8 | WNW | 12 | 5 | 7.8 | N | 7 | 2 | 11.2 | ESE | 9 | 2
203 | 이천 | 10.5 | SE | 6 | 10 | 7.9 | WSW | 3 | 5 | 7.3 | NNE | 3 | 19 | 7.7 | SSW | 7 | 14 | 11 | S | 9 | 2
211 | 인제 | 11.1 | NNE | 7 | 15 | 11.1 | S | 3 | 5 | 9.3 | N | 3 | 19 | 8.2 | S | 5 | 18 | 8.4 | S | 9 | 2
212 | 홍천 | 6.9 | SSE | 6 | 10 | 7.9 | NNW | 3 | 28 | 7.9 | W | 12 | 5 | 7.5 | W | 3 | 13 | 7.3 | W | 4 | 13
216 | 태백 | 10.9 | NNE | 9 | 18 | 9.6 | SW | 3 | 5 | 7.3 | SW | 5 | 21 | 9 | SW | 10 | 19 | 9.3 | SW | 5 | 6
217 | 정선군 | [16 empty] | 13.9 | NNE | 12 | 3
221 | 제천 | 9 | W | 4 | 23 | 9.8 | WSW | 3 | 5 | 7.9 | WNW | 12 | 5 | 8.5 | WNW | 12 | 5 | 8.5 | WSW | 4 | 27
226 | 보은 | 8.6 | NW | 3 | 12 | 8.8 | W | 3 | 28 | 8.6 | NNW | 11 | 29 | 8.6 | NNW | 4 | 22 | 9.6 | NW | 4 | 13
232 | 천안 | 12.3 | ENE | 7 | 10 | 11.8 | W | 3 | 28 | 8.8 | WSW | 4 | 25 | 9.2 | W | 12 | 5 | 10.3 | ESE | 9 | 2
235 | 보령 | 14.5 | SSW | 4 | 19 | 13.9 | SSW | 3 | 28 | 11.2 | SSW | 6 | 18 | 13.8 | SSW | 7 | 9 | 20.2 | WSW | 9 | 2
236 | 부여 | 11.4 | WNW | 4 | 20 | 11.8 | SW | 3 | 28 | 7.6 | SW | 5 | 21 | 9.6 | SW | 7 | 14 | 10.1 | WSW | 3 | 12
238 | 금산 | 8.5 | SSW | 4 | 19 | 8.3 | W | 3 | 28 | 8.4 | WNW | 6 | 8 | 7.5 | S | 2 | 13 | 8.6 | W | 3 | 20
243 | 부안 | 8.9 | SSE | 6 | 10 | 11 | SSE | 3 | 4 | 11.5 | SSW | 4 | 26 | 11.3 | SSW | 2 | 13 | 13 | S | 9 | 2
244 | 임실 | 9.7 | WNW | 4 | 20 | 9.2 | SW | 3 | 28 | 8.2 | ESE | 4 | 9 | 9.2 | SW | 2 | 13 | 9.2 | SW | 11 | 11
245 | 정읍 | 7.4 | W | 3 | 28 | 7.7 | SE | 3 | 4 | 7.1 | ESE | 8 | 22 | 7.1 | WSW | 10 | 17 | 7.4 | WSW | 3 | 20
247 | 남원 | 10.7 | NW | 3 | 18 | 10.6 | SSE | 8 | 11 | 9.9 | S | 4 | 25 | 10.9 | SSE | 4 | 20 | 9.5 | NW | 4 | 13
248 | 장수 | 10.3 | ENE | 7 | 10 | 10.5 | W | 3 | 5 | 8.8 | NNE | 4 | 9 | 10.6 | W | 7 | 9 | 9.7 | W | 7 | 24
251 | 고창군 | [8 empty] | 9.4 | SE | 8 | 22 | 7.3 | ESE | 4 | 20 | 10.4 | SE | 9 | 2
252 | 영광군 | [8 empty] | 11.4 | NW | 12 | 5 | 11.6 | NNW | 4 | 25 | 13.6 | S | 9 | 2
253 | 김해시 | [8 empty] | 11.3 | WNW | 11 | 29 | 10.2 | WNW | 4 | 22 | 18.2 | SE | 8 | 11
254 | 순창군 | [8 empty] | 11.9 | NW | 12 | 5 | 11.8 | NNW | 3 | 6 | 12.4 | NNW | 4 | 13
255 | 북창원 | [12 empty] | 9.1 | SSW | 2 | 13 | 8.8 | SSE | 8 | 11
256 | 순천 | 10.1 | WSW | 3 | 12 | 10.4 | NNE | 9 | 16 | 9.8 | WNW | 2 | 23 | 9.8 | WNW | 3 | 6 | 9.7 | NW | 12 | 3
257 | 양산시 | [12 empty] | 11.2 | NNW | 2 | 13 | 11.8 | ENE | 4 | 21
258 | 보성군 | [16 empty] | 15.8 | WNW | 12 | 3
259 | 강진군 | [12 empty] | 11.9 | WNW | 12 | 5 | 15.8 | SSE | 9 | 1
260 | 장흥 | 19.1 | E | 7 | 10 | 13.3 | NNW | 2 | 14 | 14.3 | NNW | 2 | 23 | 12.3 | NNW | 3 | 6 | 14.5 | N | 12 | 3
261 | 해남 | 19.6 | E | 7 | 10 | 15.9 | N | 9 | 16 | 12.8 | E | 4 | 9 | 12.9 | SSW | 2 | 13 | 10.3 | SSE | 9 | 1
262 | 고흥 | 11.8 | SSE | 7 | 10 | 16.2 | NW | 9 | 16 | 9.9 | NNW | 2 | 23 | 10.8 | S | 2 | 13 | 10.4 | NNW | 4 | 13
263 | 의령군 | [16 empty] | 13.9 | SW | 9 | 12
264 | 함양군 | [16 empty] | 10.5 | WSW | 12 | 3
271 | 봉화 | 10.1 | N | 9 | 18 | 8.4 | NE | 9 | 16 | 8.3 | NE | 4 | 10 | 8.6 | N | 4 | 28 | 8.8 | NNW | 12 | 25
272 | 영주 | 11.5 | NW | 4 | 19 | 13.6 | WNW | 12 | 31 | 12.1 | NW | 11 | 29 | 13.6 | NW | 4 | 22 | 14.4 | NW | 12 | 3
273 | 문경 | 10 | N | 2 | 9 | 10.6 | NNE | 3 | 5 | 8.2 | ESE | 5 | 12 | 8.3 | WNW | 12 | 5 | 10.1 | WNW | 3 | 20
276 | 청송군 | [16 empty] | 11 | N | 12 | 3
277 | 영덕 | 13.3 | NNW | 9 | 18 | 14.3 | WSW | 12 | 31 | 12.9 | N | 4 | 10 | 12.8 | NNE | 11 | 11 | 15.3 | W | 3 | 21
278 | 의성 | 10.1 | W | 4 | 23 | 12.3 | WNW | 3 | 28 | 7.9 | NW | 12 | 25 | 8.9 | WNW | 4 | 22 | 9.7 | WNW | 3 | 21
279 | 구미 | 9.2 | WNW | 11 | 15 | 11.2 | W | 3 | 28 | 7.7 | W | 6 | 8 | 8.8 | WNW | 4 | 21 | 8.7 | WNW | 3 | 21
281 | 영천 | 10.1 | NNE | 4 | 20 | 10.6 | WNW | 2 | 14 | 9.3 | WNW | 11 | 21 | 10.1 | WNW | 4 | 22 | 10 | WNW | 4 | 13
283 | 경주시 | [16 empty] | 11.8 | NW | 12 | 3
284 | 거창 | 9 | S | 4 | 30 | 10.4 | S | 3 | 28 | 8 | NW | 11 | 21 | 9.7 | N | 4 | 27 | 10.2 | WSW | 3 | 12
285 | 합천 | 7.9 | NNE | 5 | 29 | 8.3 | NE | 9 | 16 | 13.4 | N | 7 | 7 | 8.4 | S | 3 | 17 | 7.6 | NNE | 3 | 1
288 | 밀양 | 9.5 | S | 7 | 10 | 10.9 | N | 7 | 29 | 8.9 | SSW | 5 | 18 | 10.4 | S | 2 | 13 | 9.4 | WNW | 3 | 21
289 | 산청 | 15.8 | WNW | 4 | 20 | 13 | W | 3 | 5 | 10.4 | WNW | 11 | 29 | 11.1 | WNW | 1 | 23 | 11.9 | W | 3 | 20
294 | 거제 | 13.5 | SE | 7 | 10 | 10.7 | SSE | 9 | 16 | 8.9 | WNW | 2 | 23 | 10.6 | NW | 7 | 15 | 11.9 | ESE | 8 | 11
295 | 남해 | 13 | SE | 7 | 10 | 10.4 | NW | 1 | 6 | 8.6 | WNW | 4 | 26 | 8.9 | WNW | 12 | 5 | 8.5 | WNW | 3 | 2
|  | 31.3 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 27.6 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 35.5 |  |  |  | 43
지 점 |  | 2001 년 |  |  |  | 2002 년 |  |  |  | 2003 년 |  |  |  | 2004 년 |  |  |  | 2005 년
번 호 | 지 명 | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일
90 | 속 초 | 138 NNW | 6 | 30 |  | 127 NNW | 8 | 31 |  | 142 NNW | 9 | 13 |  | 173 WNW | 1 | 22 |  | 119 NE | 10 | 21
95 | 철 원 | 101 SW | 5 | 16 |  | 126 SW | 3 | 21 |  | 105 NNE | 4 | 4 |  | 127 SW | 5 | 5 |  | 120 SW | 4 | 20
98 | 동두천 | 120 W | 3 | 4 |  | 154 NNE | 8 | 31 |  | 105 W | 10 | 28 |  | 124 W | 2 | 14 |  | 125 SSW | 4 | 6
99 | 문 산 |  |  |  |  | 96 SW | 4 | 14 |  | 93 NW | 10 | 28 |  | 100 WNW | 5 | 21 |  | 101 NW | 3 | 24
100 | 대관령 | 170 W | 1 | 2 |  | 214 W | 3 | 19 |  | 182 WSW | 1 | 27 |  | 177 W | 3 | 10 |  | 185 WSW | 4 | 28
101 | 춘 천 | 76 WSW | 3 | 26 |  | 93 N | 8 | 31 |  | 95 W | 10 | 28 |  | 127 NNW | 5 | 21 |  | 100 WNW | 5 | 9
102 | 백령도 | 171 NW | 3 | 4 |  | 273 ESE | 4 | 5 |  | 228 SW | 8 | 6 |  | 226 W | 1 | 12 |  | 247 W | 11 | 28
105 | 강 릉 | 130 SW | 5 | 18 |  | 180 WSW | 11 | 11 |  | 141 WNW | 4 | 17 |  | 180 WSW | 2 | 14 |  | 135 WSW | 4 | 28
106 | 동 해 | 156 NE | 9 | 21 |  | 184 W | 1 | 7 |  | 209 NNE | 9 | 13 |  | 170 N | 8 | 19 |  | 162 N | 1 | 16
108 | 서 울 | 89 SW | 3 | 6 |  | 117 SW | 4 | 14 |  | 90 SW | 4 | 18 |  | 111 WSW | 2 | 22 |  | 110 WSW | 2 | 22
112 | 인 천 | 143 NW | 3 | 4 |  | 151 W | 3 | 22 |  | 131 NW | 1 | 27 |  | 132 WNW | 11 | 26 |  | 124 NNW | 3 | 24
114 | 원 주 | 57 WNW | 12 | 29 |  | 73 WSW | 4 | 12 |  | 81 WNW | 11 | 21 |  | 76 WNW | 3 | 30 |  | 87 SE | 6 | 2
115 | 울릉도 | 146 NNE | 3 | 22 |  | 157 SSW | 4 | 16 |  | 166 NNE | 4 | 29 |  | 216 SSW | 11 | 26 |  | 279 NE | 9 | 7
119 | 수 원 | 109 ESE | 4 | 29 |  | 153 NE | 8 | 31 |  | 88 W | 11 | 21 |  | 100 SW | 2 | 21 |  | 115 WSW | 2 | 22
121 | 영 월 | 88 SW | 3 | 26 |  | 109 ESE | 8 | 29 |  | 100 W | 11 | 21 |  | 97 W | 11 | 26 |  | 120 S | 4 | 19
127 | 충 주 | 142 W | 3 | 4 |  | 94 W | 4 | 17 |  | 101 SE | 5 | 7 |  | 107 ENE | 6 | 21 |  | 110 E | 9 | 6
129 | 서 산 | 135 ENE | 1 | 7 |  | 172 NE | 8 | 31 |  | 136 NW | 3 | 27 |  | 142 NW | 2 | 14 |  | 127 SSW | 2 | 22
130 | 울 진 | 129 W | 3 | 4 |  | 200 ENE | 8 | 31 |  | 282 ESE | 9 | 13 |  | 224 NNW | 8 | 19 |  | 180 NNW | 9 | 7
131 | 청 주 | 91 NW | 12 | 29 |  | 126 NNE | 8 | 31 |  | 109 NW | 3 | 3 |  | 124 E | 6 | 21 |  | 87 WNW | 3 | 24
133 | 대 전 | 113 NNW | 3 | 29 |  | 124 NNE | 8 | 31 |  | 164 NNW | 1 | 29 |  | 147 NW | 6 | 22 |  | 146 NNW | 2 | 1
135 | 추풍령 | 127 W | 1 | 15 |  | 182 WNW | 1 | 7 |  | 127 W | 9 | 13 |  | 130 WNW | 9 | 1 |  | 121 W | 2 | 1
136 | 안 동 | 108 WNW | 3 | 4 |  | 81 WNW | 8 | 27 |  | 91 WNW | 11 | 21 |  | 99 WNW | 2 | 14 |  | 94 W | 4 | 28
137 | 상 주 |  |  |  |  | 120 WNW | 4 | 17 |  | 155 NW | 9 | 13 |  | 105 WNW | 11 | 26 |  | 130 W | 3 | 24
138 | 포 항 | 106 W | 1 | 2 |  | 146 ENE | 8 | 31 |  | 185 SSE | 9 | 12 |  | 111 NNW | 8 | 19 |  | 101 N | 9 | 6
140 | 군 산 | 235 WNW | 3 | 4 |  | 205 NE | 8 | 31 |  | 208 NW | 1 | 3 |  | 140 NW | 11 | 26 |  | 136 NW | 4 | 20
143 | 대 구 | 86 WNW | 3 | 3 |  | 153 E | 8 | 31 |  | 171 N | 9 | 12 |  | 105 WNW | 2 | 14 |  | 100 W | 2 | 1
146 | 전 주 | 114 W | 4 | 15 |  | 136 SE | 4 | 6 |  | 105 ESE | 7 | 18 |  | 126 ESE | 4 | 18 |  | 116 SE | 4 | 19
152 | 울 산 | 111 NNW | 1 | 16 |  | 131 E | 8 | 31 |  | 183 ESE | 9 | 12 |  | 148 ENE | 8 | 19 |  | 115 NE | 9 | 6
155 | 마 산 | 91 SSW | 6 | 25 |  | 107 SSE | 8 | 31 |  | 247 SSE | 9 | 12 |  | 141 NW | 8 | 19 |  | 109 S | 4 | 10
156 | 광 주 | 122 SW | 2 | 15 |  | 152 NE | 8 | 31 |  | 137 NNE | 9 | 12 |  | 130 SW | 3 | 5 |  | 117 W | 12 | 21
159 | 부 산 | 189 WSW | 6 | 25 |  | 175 S | 8 | 31 |  | 261 S | 9 | 12 |  | 157 SW | 9 | 20 |  | 145 SW | 6 | 27
162 | 통 영 | 124 SW | 6 | 25 |  | 211 S | 8 | 31 |  | 318 S | 9 | 12 |  | 149 S | 7 | 4 |  | 145 SSW | 4 | 10
165 | 목 포 | 172 NW | 3 | 4 |  | 291 NNE | 8 | 31 |  | 208 N | 9 | 12 |  | 172 NW | 11 | 12 |  | 193 W | 12 | 21
168 | 여 수 | 262 S | 6 | 25 |  | 272 ENE | 8 | 31 |  | 359 NE | 9 | 12 |  | 204 N | 8 | 19 |  | 228 NE | 9 | 6
169 | 흑산도 | 241 N | 1 | 28 |  | 333 NNE | 8 | 31 |  | 211 S | 4 | 29 |  | 240 SSE | 9 | 12 |  | 212 SSE | 5 | 17
170 | 완 도 | 171 N | 1 | 14 |  | 252 NNE | 8 | 31 |  | 289 NNE | 9 | 12 |  | 216 SE | 7 | 4 |  | 208 NW | 12 | 21
175 | 진 도 |  |  |  |  | 232 WSW | 9 | 1 |  | 218 NW | 9 | 12 |  | 273 SSE | 7 | 4 |  | 200 SSE | 4 | 19
184 | 제 주 | 195 NNE | 12 | 25 |  | 183 NE | 8 | 31 |  | 395 NW | 9 | 12 |  | 172 NW | 12 | 4 |  | 162 NW | 12 | 21
185 | 고 산 | 317 N | 1 | 28 |  | 437 N | 8 | 31 |  | 511 N | 9 | 12 |  | 294 NNW | 12 | 5 |  | 339 NNW | 12 | 21
189 | 서귀포 | 118 SSW | 6 | 24 |  | 208 NNE | 8 | 31 |  | 160 NNW | 9 | 12 |  | 167 SSE | 7 | 4 |  | 136 ENE | 9 | 6
192 | 진 주 | 93 NNE | 2 | 25 |  | 114 E | 8 | 31 |  | 189 NNE | 9 | 12 |  | 102 NNW | 8 | 19 |  | 88 NNE | 9 | 6
201 | 강 화 | 91 N | 7 | 14 |  | 104 SW | 8 | 5 |  | 84 SW | 9 | 5 |  | 94 SW | 5 | 19 |  | 105 SW | 11 | 7
202 | 양 평 | 72 WNW | 1 | 2 |  | 67 NNE | 9 | 1 |  | 69 WNW | 1 | 29 |  | 86 WNW | 11 | 26 |  | 88 SW | 4 | 21
203 | 이 천 | 82 W | 3 | 4 |  | 119 NE | 8 | 31 |  | 88 NE | 5 | 7 |  | 79 NNE | 10 | 20 |  | 81 SSE | 6 | 1
211 | 인 제 | 112 ENE | 1 | 25 |  | 111 NE | 8 | 31 |  | 91 NE | 5 | 14 |  | 100 SSW | 4 | 25 |  | 117 N | 9 | 6
212 | 홍 천 | 87 WSW | 1 | 28 |  | 89 WNW | 3 | 22 |  | 90 S | 8 | 5 |  | 84 NW | 2 | 5 |  | 98 NNE | 8 | 17
216 | 태 백 | 112 NW | 2 | 1 |  | 117 ESE | 3 | 21 |  | 113 NNE | 9 | 13 |  | 150 NNE | 9 | 7 |  | 127 NNE | 7 | 1
221 | 제 천 | 100 ENE | 1 | 25 |  | 102 WNW | 8 | 31 |  | 135 SW | 9 | 13 |  | 98 WSW | 2 | 14 |  | 107 W | 4 | 20
226 | 보 은 | 87 NNW | 1 | 2 |  | 94 WNW | 11 | 1 |  | 108 NW | 9 | 13 |  | 87 WNW | 2 | 14 |  | 107 NW | 1 | 31
232 | 천 안 | 98 NW | 1 | 28 |  | 109 N | 8 | 31 |  | 107 WNW | 3 | 3 |  | 103 WNW | 11 | 26 |  | 112 WNW | 3 | 24
235 | 보 령 | 156 S | 2 | 15 |  | 166 N | 8 | 31 |  | 97 SSW | 10 | 28 |  | 105 SSW | 3 | 17 |  | 104 WSW | 2 | 22
236 | 부 여 | 105 SW | 2 | 15 |  | 83 WNW | 2 | 11 |  | 102 WNW | 10 | 28 |  | 118 WNW | 2 | 14 |  | 104 SW | 2 | 22
238 | 금 산 | 105 NW | 1 | 1 |  | 91 ESE | 8 | 31 |  | 62 NNE | 11 | 21 |  | 75 SSE | 4 | 18 |  | 68 SSW | 9 | 13
243 | 부 안 | 105 W | 2 | 7 |  | 91 SSW | 4 | 14 |  | 91 N | 11 | 21 |  | 104 S | 3 | 16 |  | 114 SSE | 4 | 19
244 | 임 실 | 124 SE | 1 | 7 |  | 120 N | 8 | 31 |  | 103 N | 9 | 12 |  | 74 SSW | 7 | 4 |  | 93 NNE | 9 | 6
245 | 정 읍 | 83 SSE | 1 | 14 |  | 98 NW | 8 | 31 |  | 80 E | 7 | 18 |  | 83 ESE | 4 | 18 |  | 97 SE | 5 | 17
247 | 남 원 | 104 N | 1 | 14 |  | 118 NW | 3 | 21 |  | 142 NNW | 9 | 12 |  | 104 S | 4 | 1 |  | 101 SSW | 5 | 17
248 | 장 수 | 97 SSW | 2 | 15 |  | 108 NW | 3 | 21 |  | 145 N | 9 | 12 |  | 95 E | 7 | 31 |  | 97 NNW | 12 | 17
256 | 순 천 | 93 N | 2 | 1 |  | 88 SSE | 7 | 6 |  | 130 NW | 9 | 12 |  | 77 W | 2 | 14 |  | 87 W | 12 | 17
260 | 장 흥 | 171 NNW | 2 | 1 |  | 161 E | 7 | 5 |  | 152 NW | 9 | 12 |  | 146 ESE | 7 | 4 |  | 128 ESE | 8 | 24
261 | 해 남 | 164 WNW | 1 | 14 |  | 205 N | 8 | 31 |  | 168 N | 9 | 12 |  | 161 ESE | 7 | 4 |  | 136 SE | 4 | 19
262 | 고 흥 | 127 NW | 1 | 2 |  | 67 W | 1 | 7 |  | 94 WNW | 10 | 28 |  | 100 WNW | 11 | 26 |  | 107 WNW | 3 | 13
265 | 성산포 | 127 NNW | 1 | 9 |  | 199 NNE | 8 | 31 |  | 209 NW | 9 | 12 |  | 140 S | 7 | 4 |  | 127 NNW | 10 | 22
271 | 봉 화 | 114 N | 1 | 12 |  | 82 E | 12 | 28 |  | 87 NNW | 8 | 6 |  | 81 NNW | 3 | 2 |  | 103 SSW | 4 | 28
272 | 영 주 | 139 W | 2 | 1 |  | 129 NW | 2 | 17 |  | 158 WNW | 9 | 13 |  | 113 WNW | 2 | 17 |  | 120 WNW | 1 | 31
273 | 문 경 | 108 WNW | 3 | 3 |  | 111 WNW | 3 | 21 |  | 127 NNE | 9 | 12 |  | 105 NNE | 4 | 2 |  | 100 NNW | 3 | 25
277 | 영 덕 | 182 WSW | 1 | 2 |  | 174 W | 1 | 8 |  | 154 ESE | 9 | 12 |  | 149 NNE | 10 | 20 |  | 183 NNE | 9 | 6
278 | 의 성 | 97 WNW | 1 | 2 |  | 97 WNW | 3 | 21 |  | 122 NW | 9 | 12 |  | 99 WNW | 2 | 14 |  | 93 WNW | 12 | 13
279 | 구 미 | 86 WNW | 1 | 2 |  | 92 W | 11 | 1 |  | 107 NNE | 9 | 12 |  | 90 W | 2 | 14 |  | 95 WSW | 4 | 28
281 | 영 천 | 127 WNW | 1 | 14 |  | 120 ENE | 8 | 31 |  | 149 ESE | 9 | 12 |  | 95 N | 2 | 17 |  | 105 WNW | 2 | 1
284 | 거 창 | 108 WSW | 2 | 15 |  | 124 NE | 8 | 31 |  | 138 N | 9 | 12 |  | 101 W | 11 | 26 |  | 98 W | 3 | 11
285 | 합 천 | 90 WSW | 1 | 2 |  | 93 SSE | 4 | 14 |  | 202 NE | 9 | 12 |  | 80 NNE | 8 | 19 |  | 95 NNE | 8 | 15
288 | 밀 양 | 95 E | 1 | 29 |  | 124 NW | 8 | 31 |  | 174 S | 9 | 12 |  | 108 WNW | 2 | 14 |  | 82 WNW | 12 | 17
289 | 산 청 | 103 W | 2 | 1 |  | 133 WSW | 3 | 21 |  | 155 W | 9 | 12 |  | 119 NW | 12 | 5 |  | 130 SE | 3 | 11
294 | 거 제 | 86 ENE | 1 | 7 |  | 113 WNW | 4 | 16 |  | 131 ESE | 9 | 12 |  | 92 E | 8 | 19 |  | 85 NW | 12 | 17
295 | 남 해 | 107 WSW | 1 | 2 |  | 141 E | 8 | 31 |  | 156 N | 9 | 12 |  | 97 NW | 11 | 26 |  | 84 NW | 12 | 17
지 점 |  | 1996 년 |  |  |  | 1997 년 |  |  |  | 1998 년 |  |  |  | 1999 년 |  |  |  | 2000 년
번 호 | 지 명 | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일
90 | 속 초 | 163 N | 10 | 15 |  | 183 NW | 1 | 2 |  | 193 WNW | 2 | 8 |  | 177 NW | 4 | 6 |  | 166 WNW | 1 | 7
95 | 철 원 | 160 WSW | 5 | 9 |  | 140 SSW | 1 | 1 |  | 148 ENE | 9 | 30 |  | 110 NE | 4 | 10 |  | 107 W | 4 | 7
98 | 동두천 | [8 empty] | 138 WSW | 4 | 12 |  | 150 SSW | 8 | 4 |  | 144 S | 9 | 1
100 | 대관령 | 200 W | 6 | 30 |  | 248 W | 1 | 2 |  | 190 WSW | 3 | 19 |  | 180 W | 12 | 9 |  | 242 W | 7 | 12
101 | 춘 천 | 117 ENE | 9 | 16 |  | 130 SW | 1 | 1 |  | 100 WSW | 8 | 10 |  | 110 SSW | 8 | 3 |  | 121 WSW | 1 | 7
102 | 백령도 | [16 empty] | 199 NW | 9 | 1
105 | 강 릉 | 137 WSW | 1 | 3 |  | 143 SW | 12 | 19 |  | 187 SSW | 3 | 20 |  | 167 W | 2 | 28 |  | 178 SW | 4 | 7
106 | 동 해 | 150 WNW | 2 | 5 |  | 267 WSW | 1 | 1 |  | 150 WNW | 2 | 8 |  | 158 E | 11 | 15 |  | 144 W | 4 | 11
108 | 서 울 | 117 SSW | 6 | 29 |  | 127 WNW | 3 | 29 |  | 160 SW | 4 | 12 |  | 113 S | 8 | 3 |  | 125 SSW | 9 | 1
112 | 인 천 | 178 S | 7 | 16 |  | 203 NW | 1 | 2 |  | 167 NW | 12 | 10 |  | 168 NNW | 2 | 12 |  | 192 SSW | 9 | 1
114 | 원 주 | 108 WNW | 12 | 5 |  | 100 WSW | 1 | 1 |  | 100 NE | 1 | 15 |  | 118 SE | 8 | 3 |  | 77 SSE | 8 | 31
115 | 울릉도 | 180 NNE | 6 | 18 |  | 163 N | 3 | 30 |  | 203 NNE | 10 | 18 |  | 217 NNE | 4 | 2 |  | 173 WSW | 7 | 22
119 | 수 원 | 160 SSW | 6 | 29 |  | 110 WSW | 1 | 1 |  | 103 SW | 4 | 12 |  | 130 SE | 8 | 3 |  | 133 SSW | 9 | 1
121 | 영 월 | 123 NW | 1 | 3 |  | 143 NW | 4 | 16 |  | 117 SE | 3 | 9 |  | 117 ESE | 8 | 3 |  | 107 ESE | 8 | 31
129 | 서 산 | 150 SSW | 6 | 29 |  | 142 SSW | 6 | 1 |  | 167 SSW | 6 | 25 |  | 163 ENE | 8 | 3 |  | 225 S | 8 | 31
130 | 울 진 | 138 WSW | 12 | 22 |  | 317 W | 1 | 1 |  | 157 N | 10 | 1 |  | 130 NNE | 4 | 27 |  | 160 NNW | 3 | 31
131 | 청 주 | 150 SSW | 6 | 29 |  | 127 ESE | 11 | 25 |  | 137 N | 9 | 30 |  | 173 S | 8 | 3 |  | 119 SSW | 8 | 31
133 | 대 전 | 133 SW | 6 | 29 |  | 127 E | 9 | 15 |  | 137 SSE | 9 | 5 |  | 170 SSE | 8 | 3 |  | 195 S | 8 | 31
135 | 추풍령 | 200 WSW | 12 | 22 |  | 153 W | 1 | 21 |  | 127 W | 3 | 19 |  | 123 W | 2 | 12 |  | 154 W | 3 | 24
136 | 안 동 | 120 NW | 1 | 30 |  | 117 NW | 1 | 1 |  | 110 W | 2 | 8 |  | 142 NW | 3 | 5 |  | 110 NNW | 4 | 10
138 | 포 항 | 120 W | 1 | 8 |  | 157 WNW | 1 | 2 |  | 137 NE | 1 | 15 |  | 123 W | 1 | 25 |  | 153 SSE | 9 | 16
140 | 군 산 | 210 W | 6 | 18 |  | 200 W | 1 | 1 |  | 167 W | 12 | 7 |  | 182 WSW | 2 | 2 |  | 204 WNW | 1 | 7
143 | 대 구 | 137 W | 12 | 22 |  | 143 W | 1 | 28 |  | 137 WNW | 11 | 17 |  | 167 SSE | 8 | 3 |  | 99 NW | 4 | 10
146 | 전 주 | 90 WSW | 6 | 29 |  | 93 SE | 11 | 25 |  | 127 SSE | 4 | 12 |  | 157 SE | 8 | 3 |  | 126 SSE | 8 | 31
152 | 울 산 | 87 W | 12 | 22 |  | 112 NW | 2 | 21 |  | 147 WSW | 3 | 19 |  | 147 NW | 1 | 11 |  | 116 NW | 2 | 8
155 | 마 산 | 113 S | 5 | 5 |  | 112 NNE | 9 | 14 |  | 123 SSW | 3 | 19 |  | 167 N | 11 | 1 |  | 153 S | 9 | 16
156 | 광 주 | 130 SSW | 6 | 29 |  | 153 SSW | 7 | 4 |  | 177 NNE | 9 | 30 |  | 238 SSE | 8 | 3 |  | 179 S | 3 | 28
159 | 부 산 | 217 SW | 4 | 17 |  | 208 SSW | 5 | 7 |  | 200 SW | 5 | 2 |  | 183 SW | 8 | 3 |  | 187 SSW | 9 | 16
162 | 통 영 | 138 S | 4 | 17 |  | 200 SE | 8 | 9 |  | 200 SSE | 5 | 2 |  | 217 SSE | 8 | 3 |  | 151 SSE | 9 | 16
164 | 무 안 | 126 SW | 6 | 29 |  | 111 WNW | 9 | 26 |  | 168 NNE | 9 | 30 |  | 250 SSE | 8 | 3 |  | 181 SW | 3 | 27
165 | 목 포 | 185 NW | 12 | 5 |  | 190 NNW | 1 | 21 |  | 187 NE | 9 | 30 |  | 205 S | 8 | 3 |  | 214 S | 8 | 31
168 | 여 수 | 167 N | 3 | 15 |  | 218 NNE | 9 | 16 |  | 233 NE | 9 | 30 |  | 307 S | 8 | 3 |  | 264 S | 8 | 31
169 | 흑산도 |  |  |  |  | 267 N | 1 | 21 |  | 300 NNE | 9 | 30 |  | 248 N | 2 | 3 |  | 474 S | 8 | 31
170 | 완 도 | 177 NNW | 3 | 17 |  | 157 NW | 12 | 11 |  | 217 NNW | 1 | 18 |  | 273 SSE | 8 | 3 |  | 230 SE | 8 | 31
184 | 제 주 | 160 NW | 11 | 30 |  | 157 NW | 1 | 5 |  | 160 NW | 9 | 30 |  | 223 SSW | 8 | 3 |  | 179 SSW | 3 | 28
185 | 제주고층 | 273 NW | 12 | 22 |  | 295 NW | 1 | 21 |  | 263 NNW | 9 | 30 |  | 288 NNW | 2 | 3 |  | 322 N | 2 | 8
189 | 서귀포 | 123 SW | 12 | 4 |  | 167 NNE | 9 | 15 |  | 143 S | 3 | 19 |  | 240 SSE | 8 | 3 |  | 161 SE | 8 | 31
192 | 진 주 | 128 NNW | 1 | 8 |  | 125 NNW | 1 | 21 |  | 108 N | 1 | 18 |  | 158 SSW | 8 | 3 |  | 100 NNW | 2 | 14
201 | 강 화 | 77 WSW | 7 | 26 |  | 87 WSW | 6 | 1 |  | 98 WSW | 1 | 18 |  | 135 SW | 8 | 3 |  | 127 NE | 9 | 16
202 | 양 평 | 93 NW | 7 | 1 |  | 95 W | 1 | 1 |  | 93 WNW | 10 | 19 |  | 134 SE | 8 | 3 |  | 147 WNW | 6 | 9
203 | 이 천 | 81 SW | 6 | 29 |  | 74 WNW | 12 | 10 |  | 79 N | 8 | 27 |  | 154 S | 8 | 3 |  | 112 WNW | 3 | 25
211 | 인 제 | 85 S | 11 | 27 |  | 97 S | 4 | 12 |  | 99 S | 1 | 19 |  | 122 SSW | 12 | 9 |  | 138 SSW | 4 | 7
212 | 홍 천 | 97 SW | 6 | 29 |  | 70 NW | 10 | 10 |  | 85 WNW | 11 | 9 |  | 107 SW | 8 | 3 |  | 113 S | 3 | 28
216 | 태 백 | 94 WSW | 6 | 29 |  | 110 W | 1 | 1 |  | 124 WSW | 1 | 20 |  | 124 WSW | 5 | 20 |  | 172 SW | 9 | 1
221 | 제 천 | 94 NW | 11 | 30 |  | 107 ENE | 3 | 14 |  | 83 ENE | 1 | 14 |  | 124 ENE | 3 | 19 |  | 123 WSW | 4 | 23
223 | 충 주 | 122 WNW | 12 | 22 |  | 131 N | 8 | 3 |  | 108 WNW | 1 | 24 |  | 135 SSE | 8 | 3 |  | 144 E | 7 | 4
226 | 보 은 | 99 NW | 4 | 11 |  | 64 NW | 2 | 18 |  | 95 N | 11 | 17 |  | 162 SE | 8 | 3 |  | 126 NW | 3 | 24
232 | 천 안 | 95 WNW | 11 | 30 |  | 92 E | 11 | 25 |  | 144 NW | 1 | 18 |  | 158 S | 8 | 3 |  | 140 W | 4 | 10
235 | 보 령 | 146 SSW | 6 | 29 |  | 146 SSW | 8 | 4 |  | 116 S | 8 | 23 |  | 177 NNW | 11 | 1 |  | 158 SSE | 3 | 27
236 | 부 여 | 98 SSW | 6 | 29 |  | 67 W | 1 | 1 |  | 76 SW | 4 | 12 |  | 196 SE | 8 | 3 |  | 132 S | 8 | 31
238 | 금 산 | 77 SW | 6 | 29 |  | 90 SSW | 1 | 1 |  | 94 SSW | 3 | 19 |  | 151 S | 8 | 3 |  | 115 N | 2 | 24
243 | 부 안 | 99 W | 11 | 30 |  | 109 S | 6 | 1 |  | 112 WNW | 1 | 24 |  | 173 SSE | 8 | 3 |  | 152 SSW | 8 | 31
244 | 임 실 | 91 W | 3 | 4 |  | 92 SW | 5 | 7 |  | 111 NNE | 9 | 30 |  | 193 SW | 8 | 3 |  | 115 W | 4 | 27
245 | 정 읍 | 71 ESE | 4 | 29 |  | 75 ESE | 11 | 25 |  | 79 NNE | 9 | 30 |  | 207 SSE | 8 | 3 |  | 133 ESE | 8 | 31
247 | 남 원 | 98 WNW | 12 | 22 |  | 111 SSW | 7 | 22 |  | 102 SSW | 3 | 19 |  | 237 SSE | 8 | 3 |  | 142 WNW | 4 | 10
248 | 장 수 | 99 SSW | 6 | 29 |  | 98 S | 7 | 1 |  | 88 SSW | 3 | 19 |  | 159 SSE | 8 | 3 |  | 134 SW | 9 | 16
256 | 순 천 | 86 N | 2 | 20 |  | 78 W | 12 | 8 |  | 91 W | 2 | 8 |  | 142 S | 8 | 3 |  | 114 W | 3 | 24
260 | 장 흥 | 107 WNW | 3 | 11 |  | 111 ESE | 11 | 25 |  | 188 NE | 9 | 30 |  | 239 SSE | 8 | 3 |  | 182 ESE | 8 | 31
261 | 해 남 | 138 WNW | 1 | 8 |  | 138 SE | 11 | 25 |  | 178 N | 9 | 30 |  | 227 SSE | 8 | 3 |  | 199 S | 8 | 31
262 | 고 흥 | 105 NW | 6 | 18 |  | 102 NW | 1 | 21 |  | 105 SSE | 9 | 30 |  | 250 SE | 8 | 3 |  | 162 SSW | 8 | 31
265 | 성산포 | 114 SW | 12 | 4 |  | 154 SSE | 11 | 25 |  | 148 SSE | 9 | 30 |  | 240 SE | 8 | 3 |  | 141 SSE | 8 | 31
271 | 춘 양 | 89 NW | 5 | 11 |  | 76 W | 1 | 1 |  | 110 NW | 1 | 25 |  | 100 WNW | 12 | 10 |  | 106 WSW | 9 | 1
272 | 영 주 | 155 WNW | 1 | 3 |  | 187 WNW | 12 | 10 |  | 217 WNW | 1 | 19 |  | 142 W | 5 | 19 |  | 168 WNW | 4 | 23
273 | 문 경 | 102 NW | 1 | 8 |  | 90 NW | 1 | 1 |  | 107 NW | 3 | 19 |  | 122 W | 12 | 6 |  | 152 WSW | 4 | 23
277 | 영 덕 | 105 WNW | 1 | 9 |  | 127 WNW | 1 | 2 |  | 142 NNE | 9 | 30 |  | 155 NE | 4 | 25 |  | 162 W | 2 | 8
278 | 의 성 | 99 WNW | 12 | 22 |  | 93 NNE | 12 | 8 |  | 97 NE | 9 | 30 |  | 132 SSW | 8 | 3 |  | 126 W | 4 | 10
279 | 구 미 | 79 SW | 1 | 3 |  | 69 N | 12 | 2 |  | 86 N | 1 | 24 |  | 122 WNW | 11 | 25 |  | 146 W | 9 | 16
281 | 영 천 | 96 SSE | 1 | 9 |  | 91 WNW | 11 | 17 |  | 101 WNW | 2 | 8 |  | 116 S | 8 | 3 |  | 184 SE | 9 | 16
284 | 거 창 | 96 NW | 12 | 22 |  | 90 NW | 1 | 2 |  | 85 NNE | 1 | 24 |  | 151 ESE | 8 | 3 |  | 139 SW | 4 | 23
285 | 합 천 | 80 NNW | 1 | 8 |  | 97 SSW | 2 | 28 |  | 78 SSE | 3 | 19 |  | 143 SSE | 8 | 3 |  | 163 NNE | 9 | 16
288 | 밀 양 | 92 WSW | 12 | 22 |  | 91 S | 1 | 1 |  | 121 S | 3 | 19 |  | 154 SSE | 8 | 3 |  | 212 NW | 9 | 16
289 | 산 청 | 104 WNW | 12 | 22 |  | 117 WNW | 2 | 21 |  | 127 NNW | 1 | 24 |  | 126 W | 4 | 13 |  | 158 WNW | 3 | 24
294 | 거 제 | 100 W | 1 | 8 |  | 84 NNW | 8 | 5 |  | 88 SE | 9 | 30 |  | 130 WNW | 6 | 23 |  | 153 WNW | 9 | 1
295 | 남 해 | 102 WNW | 12 | 22 |  | 117 NW | 1 | 1 |  | 109 WNW | 2 | 8 |  | 142 ESE | 8 | 3 |  | 153 SSW | 8 | 31
지 점 |  | 1991 년 |  |  |  | 1992 년 |  |  |  | 1993 년 |  |  |  | 1994 년 |  |  |  | 1995 년
번 호 | 지 명 | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일
90 | 속 초 | 173 W | 5 | 18 |  | 187 W | 4 | 23 |  | 167 N | 5 | 12 |  | 183 NNW | 10 | 12 |  | 178 WNW | 4 | 26
95 | 철 원 | 140 W | 10 | 18 |  | 133 WSW | 4 | 23 |  | 137 SW | 4 | 26 |  | 133 NNE | 6 | 19 |  | 163 SW | 5 | 4
98 | 동두천
99 | 문 산
100 | 대관령 | 227 W | 5 | 18 |  | 200 W | 11 | 15 |  | 205 W | 4 | 26 |  | 205 W | 11 | 6 |  | 183 W | 5 | 5
101 | 춘 천 | 110 WSW | 5 | 1 |  | 103 W | 4 | 24 |  | 127 NNW | 3 | 28 |  | 107 WSW | 4 | 13 |  | 123 WSW | 4 | 25
102 | 백령도
105 | 강 릉 | 127 WSW | 4 | 30 |  | 133 WSW | 12 | 21 |  | 133 WNW | 12 | 21 |  | 167 NW | 4 | 2 |  | 163 W | 1 | 9
106 | 동 해 |  |  |  |  | 128 WSW | 12 | 21 |  | 143 WSW | 4 | 17 |  | 140 N | 12 | 9 |  | 187 W | 4 | 26
108 | 서 울 | 133 SW | 4 | 30 |  | 120 WNW | 11 | 13 |  | 152 SW | 4 | 26 |  | 103 NW | 10 | 3 |  | 103 SW | 3 | 20
112 | 인 천 | 163 SE | 7 | 20 |  | 150 NW | 11 | 15 |  | 137 NW | 2 | 7 |  | 143 WSW | 10 | 3 |  | 138 W | 12 | 24
114 | 원 주 | 100 WSW | 4 | 30 |  | 93 SE | 5 | 7 |  | 117 SSE | 6 | 2 |  | 110 SSE | 3 | 22 |  | 133 SW | 5 | 5
115 | 울릉도 | 237 NE | 9 | 27 |  | 297 N | 9 | 25 |  | 257 N | 8 | 10 |  | 278 NNE | 10 | 21 |  | 163 NNE | 11 | 10
119 | 수 원 | 133 SW | 6 | 11 |  | 123 SW | 4 | 23 |  | 95 WSW | 4 | 26 |  | 90 SSW | 5 | 28 |  | 128 S | 8 | 27
121 | 영 월 | [16 empty] | 150 SW | 4 | 25
127 | 충 주 | 85 NNW | 7 | 20 |  | 82 NW | 12 | 13 |  | 105 WNW | 12 | 21 |  | 102 WNW | 2 | 21 |  | 103 SW | 1 | 9
129 | 서 산 | 155 NW | 2 | 21 |  | 167 NW | 12 | 21 |  | 167 W | 4 | 22 |  | 157 N | 10 | 12 |  | 157 WSW | 3 | 20
130 | 울 진 | 173 NW | 7 | 20 |  | 190 ESE | 9 | 24 |  | 227 NW | 8 | 10 |  | 220 ESE | 10 | 12 |  | 217 E | 7 | 23
131 | 청 주 | 83 NNE | 1 | 2 |  | 113 WNW | 4 | 15 |  | 110 SSW | 10 | 22 |  | 117 SSW | 4 | 12 |  | 132 WSW | 5 | 5
133 | 대 전 | 110 E | 8 | 23 |  | 127 SE | 8 | 12 |  | 133 WSW | 6 | 2 |  | 115 SW | 8 | 1 |  | 160 S | 8 | 26
135 | 추풍령 | 200 W | 5 | 1 |  | 187 WSW | 12 | 13 |  | 167 W | 4 | 26 |  | 173 W | 2 | 28 |  | 137 WNW | 11 | 7
136 | 안 동 | 167 NW | 2 | 21 |  | 125 NW | 12 | 13 |  | 117 SW | 12 | 21 |  | 117 NW | 12 | 2 |  | 137 NW | 11 | 7
137 | 상 주
138 | 포 항 | 173 NNE | 10 | 14 |  | 150 NE | 1 | 31 |  | 133 NNE | 3 | 28 |  | 133 SSE | 10 | 12 |  | 113 SSW | 7 | 24
140 | 군 산 | 243 W | 12 | 28 |  | 250 W | 4 | 12 |  | 235 WSW | 6 | 2 |  | 220 WNW | 2 | 9 |  | 223 WNW | 11 | 7
143 | 대 구 | 157 WNW | 12 | 28 |  | 162 WNW | 1 | 18 |  | 140 W | 4 | 7 |  | 130 S | 7 | 15 |  | 137 WNW | 11 | 7
146 | 전 주 | 83 NE | 8 | 23 |  | 110 SSE | 5 | 6 |  | 107 SE | 7 | 10 |  | 110 SSE | 3 | 7 |  | 87 S | 3 | 16
152 | 울 산 | 100 NE | 8 | 23 |  | 87 SSE | 9 | 24 |  | 97 ENE | 8 | 10 |  | 123 ENE | 6 | 19 |  | 100 N | 11 | 7
155 | 마 산 | 140 WNW | 7 | 29 |  | 133 SSE | 9 | 24 |  | 130 NW | 8 | 10 |  | 130 WNW | 2 | 9 |  | 223 SE | 7 | 23
156 | 광 주 | 133 SSE | 5 | 6 |  | 120 SSW | 7 | 21 |  | 135 SSW | 4 | 26 |  | 150 SE | 8 | 1 |  | 177 NNE | 7 | 23
159 | 부 산 | 183 N | 9 | 27 |  | 200 SW | 9 | 24 |  | 177 WSW | 6 | 2 |  | 217 SSW | 10 | 12 |  | 225 S | 7 | 23
162 | 통 영 | 220 SW | 4 | 17 |  | 175 W | 12 | 21 |  | 173 SW | 4 | 23 |  | 223 SSE | 10 | 12 |  | 243 SE | 7 | 23
165 | 목 포 | 193 NW | 2 | 21 |  | 173 NW | 12 | 10 |  | 187 S | 4 | 23 |  | 200 NW | 10 | 12 |  | 203 NNW | 3 | 10
168 | 여 수 | 233 N | 8 | 23 |  | 167 WNW | 1 | 9 |  | 177 N | 9 | 3 |  | 200 WNW | 2 | 9 |  | 332 N | 7 | 23
169 | 흑산도
170 | 완 도 | 177 N | 1 | 2 |  | 160 NNW | 12 | 13 |  | 173 N | 10 | 29 |  | 190 NNW | 2 | 21 |  | 233 WNW | 7 | 23
175 | 진 도
184 | 제 주 | 167 N | 9 | 27 |  | 180 SSW | 5 | 7 |  | 177 WNW | 12 | 26 |  | 167 NW | 2 | 9 |  | 173 SW | 4 | 22
185 | 고 산 | 243 NNW | 9 | 27 |  | 252 N | 1 | 31 |  | 268 N | 4 | 24 |  | 232 NW | 2 | 9 |  | 237 NW | 3 | 10
189 | 서귀포 | 157 NE | 7 | 29 |  | 127 SSW | 9 | 24 |  | 153 ENE | 8 | 9 |  | 177 ENE | 8 | 13 |  | 130 SSW | 4 | 21
192 | 진 주 | 127 NNE | 8 | 23 |  | 130 NNW | 10 | 25 |  | 130 NW | 2 | 7 |  | 123 SSE | 10 | 12 |  | 167 S | 7 | 23
201 | 강 화 | 90 NNW | 5 | 1 |  | 96 SW | 9 | 2 |  | 94 W | 4 | 26 |  | 93 NNW | 2 | 9 |  | 87 ENE | 8 | 26
202 | 양 평 | 105 SW | 2 | 21 |  | 75 SW | 4 | 23 |  | 88 WNW | 12 | 16 |  | 82 W | 4 | 13 |  | 93 SW | 5 | 5
203 | 이 천 | 70 SW | 7 | 25 |  | 63 W | 12 | 13 |  | 66 SSW | 4 | 26 |  | 88 NE | 8 | 1 |  | 104 WNW | 11 | 23
211 | 인 제 | 90 SSW | 4 | 30 |  | 115 S | 4 | 23 |  | 108 NNW | 5 | 13 |  | 108 SSW | 4 | 13 |  | 137 S | 4 | 8
212 | 홍 천 | 85 SW | 4 | 30 |  | 80 WSW | 4 | 24 |  | 87 SSE | 9 | 22 |  | 65 WNW | 4 | 14 |  | 92 SSW | 8 | 27
216 | 태 백 | 127 NNW | 8 | 23 |  | 112 SSW | 5 | 7 |  | 111 SW | 6 | 2 |  | 105 WSW | 8 | 1 |  | 97 W | 8 | 27
221 | 제 천 | 90 W | 4 | 30 |  | 100 NW | 7 | 2 |  | 85 E | 3 | 15 |  | 76 NW | 12 | 18 |  | 85 WNW | 4 | 23
226 | 보 은 | 110 W | 12 | 11 |  | 100 NW | 4 | 24 |  | 95 NW | 2 | 22 |  | 105 NW | 2 | 21 |  | 108 WNW | 11 | 7
232 | 천 안 | 90 WNW | 12 | 28 |  | 95 WNW | 1 | 17 |  | 99 W | 4 | 22 |  | 93 E | 4 | 21 |  | 85 SW | 8 | 9
235 | 보 령 | 115 SSW | 7 | 25 |  | 125 WSW | 4 | 28 |  | 88 SSW | 6 | 2 |  | 104 SSW | 5 | 3 |  | 187 SW | 8 | 26
236 | 부 여 | 90 SW | 7 | 23 |  | 65 W | 4 | 15 |  | 118 SSW | 6 | 2 |  | 87 SSE | 8 | 1 |  | 101 SSE | 8 | 26
238 | 금 산 | 70 WSW | 4 | 30 |  | 74 W | 12 | 13 |  | 85 SW | 6 | 2 |  | 85 SSE | 8 | 1 |  | 85 W | 11 | 7
243 | 부 안 | 95 SSE | 7 | 22 |  | 115 SSE | 4 | 18 |  | 105 S | 4 | 22 |  | 131 S | 8 | 1 |  | 116 SSW | 8 | 26
244 | 임 실 | 90 ENE | 8 | 23 |  | 90 WSW | 4 | 12 |  | 90 WNW | 7 | 11 |  | 82 WNW | 4 | 13 |  | 65 W | 3 | 10
245 | 정 읍 | 85 E | 5 | 6 |  | 75 SE | 4 | 21 |  | 79 SSW | 4 | 26 |  | 75 SE | 8 | 1 |  | 33 ESE | 3 | 9
247 | 남 원 | 75 W | 5 | 2 |  | 75 SW | 12 | 10 |  | 101 WNW | 2 | 28 |  | 120 NNW | 2 | 21 |  | 122 NNW | 7 | 23
248 | 장 수 | 105 S | 5 | 6 |  | 100 SSW | 4 | 17 |  | 131 SW | 6 | 2 |  | 105 S | 8 | 1 |  | 109 SSW | 8 | 26
256 | 순 천 | 90 NW | 2 | 19 |  | 80 NW | 4 | 24 |  | 85 W | 2 | 28 |  | 94 NNW | 2 | 21 |  | 125 NNE | 7 | 23
260 | 장 흥 | 95 ESE | 5 | 6 |  | 110 SSE | 9 | 1 |  | 136 SSE | 6 | 2 |  | 134 SSE | 8 | 10 |  | 116 WNW | 11 | 14
261 | 해 남 | 165 E | 3 | 7 |  | 153 ESE | 6 | 4 |  | 107 WNW | 2 | 22 |  | 142 SE | 8 | 10 |  | 135 ESE | 5 | 13
262 | 고 흥 | 80 SW | 7 | 29 |  | 63 N | 12 | 10 |  | 73 NNW | 2 | 7 |  | 116 ENE | 10 | 11 |  | 97 NNW | 12 | 24
265 | 성산포 | 140 NNE | 7 | 29 |  | 150 W | 4 | 10 |  | 120 SE | 6 | 2 |  | 152 SSE | 10 | 11 |  | 159 NNW | 7 | 23
271 | 봉 화 | 90 ENE | 8 | 23 |  | 80 N | 5 | 23 |  | 107 NNE | 8 | 10 |  | 85 NW | 2 | 21 |  | 84 W | 3 | 10
272 | 영 주 | 140 NW | 1 | 5 |  | 143 WNW | 12 | 23 |  | 138 WNW | 12 | 22 |  | 136 WNW | 12 | 2 |  | 167 WNW | 11 | 7
273 | 문 경 | 90 SE | 3 | 26 |  | 92 NNW | 12 | 21 |  | 125 NW | 12 | 17 |  | 116 NW | 3 | 23 |  | 112 NW | 11 | 7
277 | 영 덕 | 130 NE | 8 | 23 |  | 150 NE | 4 | 10 |  | 131 NNE | 8 | 10 |  | 110 NE | 6 | 19 |  | 108 WNW | 1 | 9
278 | 의 성 | 135 NW | 2 | 21 |  | 115 NW | 4 | 15 |  | 87 W | 2 | 22 |  | 86 WNW | 12 | 2 |  | 118 WNW | 11 | 7
279 | 구 미 | 145 WNW | 2 | 21 |  | 130 WNW | 4 | 15 |  | 105 NNW | 12 | 21 |  | 126 NNW | 2 | 21 |  | 100 SSW | 11 | 7
281 | 영 천 | 117 ENE | 8 | 23 |  | 96 NW | 12 | 13 |  | 108 WNW | 2 | 23 |  | 90 WNW | 2 | 21 |  | 116 ESE | 7 | 23
284 | 거 창 | 85 W | 2 | 21 |  | 83 WNW | 12 | 13 |  | 84 WNW | 2 | 23 |  | 90 WNW | 2 | 21 |  | 80 W | 3 | 10
285 | 합 천 | 90 S | 3 | 20 |  | 82 S | 6 | 10 |  | 106 N | 8 | 10 |  | 84 SSW | 4 | 15 |  | 107 NE | 7 | 23
288 | 밀 양 | 100 NW | 5 | 16 |  | 97 WNW | 12 | 13 |  | 106 NW | 2 | 22 |  | 106 SSE | 10 | 12 |  | 135 SE | 7 | 23
289 | 산 청 | 100 W | 2 | 11 |  | 102 WNW | 11 | 20 |  | 108 NW | 2 | 22 |  | 122 WNW | 2 | 9 |  | 115 WNW | 3 | 10
294 | 거 제 | 110 SE | 4 | 17 |  | 100 SSE | 5 | 11 |  | 103 SE | 6 | 2 |  | 123 SE | 10 | 12 |  | 151 SE | 7 | 23
295 | 남 해 | 185 N | 2 | 21 |  | 155 N | 4 | 12 |  | 100 NW | 4 | 24 |  | 124 W | 8 | 11 |  | 184 NNW | 7 | 23
지 점 |  | 1986 년 |  |  |  | 1987 년 |  |  |  | 1988 년 |  |  |  | 1989 년 |  |  |  | 1990 년
번 호 | 지 명 | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일
90 | 속 초 | 217 E | 8 | 28 |  | 207 ENE | 7 | 16 |  | 167 WSW | 4 | 25 |  | 167 N | 10 | 31 |  | 218 WNW | 12 | 26
95 | 철 원 | [8 empty] | 75 N | 5 | 8 |  | 77 WSW | 11 | 27 |  | 110 SW | 12 | 26
98 | 동두천
100 | 대관령 | 183 W | 12 | 10 |  | 257 W | 4 | 21 |  | 237 WSW | 11 | 12 |  | 227 WSW | 3 | 31 |  | 283 W | 4 | 8
101 | 춘 천 | 123 SW | 5 | 6 |  | 123 SSW | 5 | 4 |  | 123 WSW | 10 | 12 |  | 90 SSW | 5 | 13 |  | 113 SSW | 12 | 25
105 | 강 릉 | 153 SW | 5 | 8 |  | 177 SW | 4 | 21 |  | 167 WSW | 4 | 13 |  | 143 SW | 5 | 16 |  | 153 W | 4 | 8
106 | 동 해
108 | 서 울 | 117 W | 1 | 3 |  | 133 S | 4 | 21 |  | 140 WNW | 10 | 12 |  | 133 SW | 3 | 31 |  | 133 WSW | 12 | 21
112 | 인 천 | 207 WSW | 1 | 3 |  | 197 WSW | 4 | 21 |  | 170 SSW | 8 | 28 |  | 170 W | 11 | 18 |  | 193 SSW | 9 | 2
114 | 원 주 | 123 SSE | 5 | 13 |  | 113 WNW | 3 | 25 |  | 87 WSW | 1 | 27 |  | 90 WNW | 3 | 10 |  | 102 WSW | 4 | 8
115 | 울릉도 | 217 NE | 10 | 2 |  | 310 NNE | 2 | 3 |  | 177 NNE | 11 | 29 |  | 193 SW | 12 | 4 |  | 267 NE | 12 | 11
119 | 수 원 | 120 W | 4 | 11 |  | 150 W | 4 | 21 |  | 107 W | 1 | 22 |  | 108 WNW | 11 | 18 |  | 130 W | 12 | 1
121 | 영 월
129 | 서 산 | 143 NNE | 8 | 28 |  | 142 NNE | 7 | 15 |  | 168 WSW | 11 | 12 |  | 167 SSW | 9 | 17 |  | 138 WNW | 12 | 25
130 | 울 진 | 280 SE | 8 | 28 |  | 280 SW | 4 | 21 |  | 147 W | 2 | 2 |  | 170 NNW | 4 | 27 |  | 257 W | 12 | 2
131 | 청 주 | 140 SSW | 8 | 28 |  | 150 NNE | 7 | 16 |  | 128 SSW | 8 | 5 |  | 183 SSW | 8 | 30 |  | 150 W | 5 | 31
133 | 대 전 | 108 W | 1 | 23 |  | 142 WSW | 4 | 21 |  | 140 WSW | 11 | 12 |  | 133 ENE | 2 | 17 |  | 133 E | 3 | 25
135 | 추풍령 | 120 NNE | 8 | 28 |  | 133 W | 12 | 30 |  | 133 W | 4 | 14 |  | 143 W | 11 | 19 |  | 157 W | 4 | 8
136 | 안 동 | 185 SSE | 8 | 28 |  | 168 W | 4 | 21 |  | 167 NW | 2 | 2 |  | 117 NW | 7 | 20 |  | 113 WNW | 12 | 25
138 | 포 항 | 167 N | 12 | 15 |  | 230 N | 8 | 31 |  | 150 NNE | 9 | 5 |  | 150 NNE | 8 | 2 |  | 150 NNE | 9 | 19
140 | 군 산 | 227 W | 8 | 29 |  | 267 WNW | 7 | 16 |  | 218 WNW | 1 | 22 |  | 217 W | 10 | 31 |  | 275 W | 12 | 1
143 | 대 구 | 203 SE | 8 | 28 |  | 197 WSW | 4 | 21 |  | 160 W | 4 | 18 |  | 133 WNW | 3 | 16 |  | 135 WSW | 1 | 10
146 | 전 주 | 143 SE | 8 | 28 |  | 100 SSE | 8 | 7 |  | 113 SSE | 3 | 11 |  | 97 SSE | 6 | 14 |  | 100 SSE | 9 | 2
152 | 울 산 | 110 S | 8 | 28 |  | 183 NNW | 8 | 31 |  | 150 WSW | 4 | 19 |  | 143 NNW | 1 | 28 |  | 130 WNW | 4 | 8
155 | 마 산 | 177 E | 8 | 28 |  | 253 S | 7 | 16 |  | 123 SW | 4 | 19 |  | 167 ESE | 7 | 28 |  | 110 WNW | 12 | 26
156 | 광 주 | 157 SSW | 7 | 11 |  | 130 SSW | 4 | 21 |  | 110 NNW | 11 | 24 |  | 120 NNW | 3 | 6 |  | 143 SE | 4 | 12
159 | 부 산 | 217 SSE | 8 | 28 |  | 257 SSW | 7 | 16 |  | 160 SSW | 4 | 19 |  | 155 WSW | 3 | 31 |  | 157 SW | 6 | 25
162 | 통 영 | 237 S | 8 | 28 |  | 267 SSW | 7 | 16 |  | 193 SSW | 4 | 19 |  | 170 S | 2 | 28 |  | 188 SSW | 6 | 26
164 | 무 안
165 | 목 포 | 257 S | 8 | 28 |  | 248 NNW | 7 | 15 |  | 200 NNW | 4 | 23 |  | 188 S | 6 | 5 |  | 213 WNW | 12 | 1
168 | 여 수 | 203 S | 8 | 28 |  | 250 SSE | 7 | 15 |  | 177 NNE | 7 | 26 |  | 233 NNE | 7 | 28 |  | 173 N | 11 | 30
169 | 흑산도
170 | 완 도 | 273 SE | 8 | 28 |  | 267 N | 8 | 30 |  | 200 NNW | 4 | 23 |  | 190 NNW | 3 | 6 |  | 200 NNW | 11 | 9
184 | 제 주 | 190 SSE | 8 | 28 |  | 240 NW | 1 | 12 |  | 177 NW | 12 | 16 |  | 183 WNW | 11 | 18 |  | 200 WNW | 12 | 1
185 | 제주고층 | [8 empty] | 218 N | 10 | 12 |  | 230 N | 2 | 26 |  | 230 N | 11 | 20
189 | 서귀포 | 250 SSE | 8 | 28 |  | 262 NNW | 8 | 31 |  | 127 ENE | 9 | 24 |  | 127 ENE | 8 | 1 |  | 145 E | 10 | 6
192 | 진 주 | 120 SSW | 8 | 28 |  | 177 SSE | 7 | 15 |  | 167 S | 4 | 19 |  | 140 SSE | 7 | 28 |  | 103 SSW | 6 | 26
201 | 강 화 | 110 SW | 4 | 6 |  | 115 W | 4 | 21 |  | 85 NW | 4 | 9 |  | 55 WSW | 11 | 18 |  | 105 NNE | 12 | 1
202 | 양 평 | 110 WNW | 4 | 11 |  | 120 WNW | 3 | 25 |  | 110 WSW | 4 | 18 |  | 95 WSW | 3 | 10 |  | 110 WSW | 12 | 26
203 | 이 천 | 65 W | 4 | 11 |  | 75 NNE | 7 | 16 |  | 65 WNW | 4 | 18 |  | 60 SSW | 6 | 29 |  | 65 SW | 4 | 25
211 | 인 제 | 115 SW | 1 | 4 |  | 135 SW | 4 | 21 |  | 105 S | 4 | 18 |  | 105 NNW | 4 | 15 |  | 120 SW | 4 | 8
212 | 홍 천 | 70 WSW | 4 | 6 |  | 70 SW | 4 | 21 |  | 75 SW | 5 | 12 |  | 95 NE | 4 | 15 |  | 100 WSW | 5 | 31
216 | 태 백 | 100 SSW | 12 | 31 |  | 153 SSW | 4 | 21 |  | 147 S | 4 | 12 |  | 117 SSW | 5 | 16 |  | 120 N | 5 | 23
221 | 제 천 | 90 SW | 4 | 11 |  | 95 SW | 4 | 21 |  | 105 SW | 4 | 14 |  | 75 SSW | 11 | 29 |  | 100 S | 4 | 8
223 | 충 주 | 75 NE | 8 | 28 |  | 75 N | 7 | 16 |  | 75 NW | 2 | 6 |  | 100 NW | 10 | 12 |  | 90 NW | 5 | 14
226 | 보 은 | 100 E | 8 | 28 |  | 100 N | 8 | 31 |  | 115 NW | 4 | 18 |  | 100 NW | 2 | 1 |  | 100 NW | 12 | 25
232 | 천 안 | 90 WSW | 2 | 27 |  | 115 WSW | 3 | 25 |  | 90 W | 1 | 8 |  | 85 N | 11 | 18 |  | 80 SW | 12 | 26
235 | 보 령 | 140 SSW | 8 | 28 |  | 170 NNE | 7 | 15 |  | 105 SSW | 4 | 19 |  | 160 SSW | 9 | 17 |  | 125 S | 9 | 2
236 | 부 여 | 100 E | 5 | 13 |  | 130 SSW | 4 | 21 |  | 90 NW | 11 | 2 |  | 145 SSE | 8 | 30 |  | 105 WNW | 4 | 8
238 | 금 산 | 95 S | 8 | 28 |  | 110 SW | 4 | 21 |  | 85 WSW | 11 | 12 |  | 75 SW | 9 | 17 |  | 85 W | 4 | 8
243 | 부 안 | 125 S | 8 | 28 |  | 130 NNE | 7 | 15 |  | 120 S | 4 | 19 |  | 105 SSE | 3 | 3 |  | 125 S | 9 | 2
244 | 임 실 | 95 S | 8 | 28 |  | 110 SSE | 8 | 7 |  | 90 SSW | 4 | 19 |  | 110 SE | 5 | 11 |  | 85 SSW | 5 | 31
245 | 정 읍 | 100 SSW | 8 | 28 |  | 70 SE | 4 | 6 |  | 65 S | 4 | 19 |  | 75 SSE | 3 | 3 |  | 75 SE | 9 | 2
247 | 남 원 | 110 S | 8 | 28 |  | 90 W | 4 | 21 |  | 85 W | 4 | 19 |  | 80 WNW | 2 | 2 |  | 80 SW | 12 | 22
248 | 장 수 | [8 empty] | 100 SSW | 4 | 19 |  | 95 NE | 7 | 28 |  | 90 SSW | 5 | 31
256 | 순 천 | 115 SE | 8 | 28 |  | 145 NW | 8 | 31 |  | 100 NNW | 10 | 12 |  | 95 NW | 5 | 14 |  | 100 SW | 4 | 8
260 | 장 흥 | 190 SSE | 8 | 28 |  | 90 NW | 4 | 21 |  | 95 NW | 2 | 2 |  | 90 SE | 6 | 4 |  | 100 SE | 4 | 12
261 | 해 남 | 130 ESE | 8 | 28 |  | 110 NNE | 8 | 30 |  | 110 SE | 5 | 7 |  | 135 ESE | 5 | 11 |  | 130 E | 5 | 2
262 | 고 흥 | 105 E | 8 | 28 |  | 150 ENE | 7 | 15 |  | 110 ENE | 5 | 20 |  | 90 NE | 7 | 28 |  | 80 ENE | 5 | 2
265 | 성산포 | 200 SE | 8 | 28 |  | 180 N | 8 | 31 |  | 115 E | 7 | 26 |  | 105 NW | 5 | 14 |  | 105 NW | 12 | 26
271 | 춘 양 | [8 empty] | 77 NW | 11 | 25 |  | 73 NE | 4 | 27 |  | 90 NNW | 11 | 6
272 | 영 주 | 165 NW | 1 | 6 |  | 150 NW | 1 | 14 |  | 160 NW | 11 | 10 |  | 120 NW | 12 | 26 |  | 145 NW | 4 | 7
273 | 문 경 | 110 WSW | 4 | 6 |  | 150 SW | 4 | 21 |  | 90 WNW | 11 | 24 |  | 80 NW | 12 | 26 |  | 115 NNW | 5 | 14
277 | 영 덕 | 130 SSE | 8 | 28 |  | 140 ESE | 7 | 16 |  | 110 W | 2 | 2 |  | 115 NNE | 4 | 27 |  | 125 NNE | 3 | 24
278 | 의 성 | 125 NW | 4 | 6 |  | 120 W | 4 | 21 |  | 95 NW | 4 | 18 |  | 115 WNW | 11 | 19 |  | 115 WNW | 12 | 22
279 | 구 미 | 145 WNW | 4 | 6 |  | 170 W | 4 | 21 |  | 140 NW | 2 | 6 |  | 125 NW | 4 | 17 |  | 140 WNW | 12 | 26
281 | 영 천 | 115 WNW | 1 | 4 |  | 150 SSE | 7 | 16 |  | 140 NW | 2 | 2 |  | 135 ESE | 8 | 29 |  | 110 NW | 12 | 11
284 | 거 창 | 110 SE | 8 | 28 |  | 105 NNW | 8 | 31 |  | 95 N | 2 | 15 |  | 85 NW | 1 | 27 |  | 75 WSW | 4 | 5
285 | 합 천 | 130 SSE | 8 | 28 |  | 125 N | 8 | 31 |  | 90 WNW | 10 | 13 |  | 100 S | 3 | 30 |  | 95 NE | 11 | 29
288 | 밀 양 | 165 S | 8 | 28 |  | 150 SSE | 7 | 15 |  | 90 SSW | 4 | 19 |  | 110 S | 8 | 29 |  | 90 NW | 12 | 26
289 | 산 청 | 75 E | 8 | 28 |  | 125 WNW | 4 | 21 |  | 80 NW | 4 | 18 |  | 65 W | 12 | 30 |  | 105 W | 4 | 8
294 | 거 제 | 170 SSW | 8 | 28 |  | 190 NW | 8 | 31 |  | 110 SE | 4 | 12 |  | 90 SE | 7 | 28 |  | 95 SSE | 5 | 31
295 | 남 해 | 180 SE | 8 | 28 |  | 175 S | 7 | 15 |  | 120 S | 4 | 12 |  | 160 NNE | 7 | 28 |  | 155 S | 6 | 25
지 점 |  | 1981 년 |  |  |  | 1982 년 |  |  |  | 1983 년 |  |  |  | 1984 년 |  |  |  | 1985 년
번 호 | 지 명 | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일
90 | 속 초 | 217 WSW | 4 | 27 |  | 197 W | 1 | 11 |  | 257 SW | 4 | 27 |  | 167 WSW | 10 | 20 |  | 187 WSW | 2 | 21
95 | 철 원
98 | 동두천
100 | 대관령 | 200 WNW | 3 | 7 |  | 157 W | 1 | 12 |  | 197 WSW | 4 | 27 |  | 137 W | 2 | 2 |  | 183 WNW | 2 | 20
101 | 춘 천 | 133 ENE | 5 | 29 |  | 123 WSW | 5 | 16 |  | 143 SW | 4 | 29 |  | 117 S | 2 | 26 |  | 110 W | 2 | 23
105 | 강 릉 | 140 W | 10 | 23 |  | 143 WSW | 5 | 4 |  | 210 SSW | 4 | 27 |  | 150 SW | 3 | 25 |  | 123 SW | 11 | 10
106 | 동 해
108 | 서 울 | 150 W | 2 | 25 |  | 130 WSW | 11 | 11 |  | 168 SW | 4 | 26 |  | 137 NNW | 7 | 15 |  | 123 SSW | 8 | 14
112 | 인 천 | 187 WNW | 1 | 2 |  | 167 SW | 12 | 22 |  | 212 SSW | 4 | 29 |  | 167 SSW | 2 | 1 |  | 200 E | 8 | 14
114 | 원 주 | 85 N | 10 | 23 |  | 85 W | 5 | 4 |  | 125 WNW | 4 | 27 |  | 90 S | 4 | 25 |  | 90 NW | 2 | 23
115 | 울릉도 | 260 SSW | 7 | 9 |  | 220 S | 12 | 22 |  | 273 SSW | 4 | 27 |  | 237 NE | 1 | 3 |  | 227 SSW | 8 | 11
119 | 수 원 | 95 W | 3 | 15 |  | 93 WNW | 7 | 26 |  | 113 W | 4 | 29 |  | 100 SSW | 6 | 6 |  | 123 S | 8 | 14
121 | 영 월
129 | 서 산 | 103 WNW | 10 | 9 |  | 137 SW | 11 | 11 |  | 137 S | 4 | 26 |  | 120 SSW | 6 | 17 |  | 143 S | 10 | 12
130 | 울 진 | 200 W | 1 | 1 |  | 217 W | 5 | 4 |  | 350 SW | 4 | 27 |  | 180 WNW | 3 | 25 |  | 213 SE | 8 | 10
131 | 청 주 | 123 SW | 4 | 23 |  | 123 WSW | 5 | 4 |  | 177 WSW | 4 | 26 |  | 113 SW | 4 | 17 |  | 97 SW | 4 | 19
133 | 대 전 | 123 SSW | 4 | 26 |  | 100 W | 4 | 16 |  | 140 WSW | 4 | 26 |  | 107 SSE | 4 | 18 |  | 110 ENE | 4 | 11
135 | 추풍령 | 147 W | 3 | 15 |  | 167 W | 1 | 12 |  | 183 W | 4 | 26 |  | 147 WNW | 2 | 7 |  | 140 W | 4 | 4
136 | 안 동 | [8 empty] | 147 WNW | 4 | 26 |  | 130 W | 3 | 29 |  | 130 WNW | 2 | 23
138 | 포 항 | 180 N | 5 | 9 |  | 167 NNE | 4 | 27 |  | 177 NE | 9 | 28 |  | 147 NE | 4 | 19 |  | 180 N | 4 | 12
140 | 군 산 | 237 NW | 2 | 25 |  | 217 W | 12 | 22 |  | 247 WSW | 3 | 17 |  | 203 WNW | 10 | 20 |  | 187 W | 11 | 11
143 | 대 구 | 180 NNW | 12 | 1 |  | 167 NW | 1 | 12 |  | 160 WSW | 4 | 26 |  | 143 WNW | 2 | 8 |  | 147 NE | 10 | 5
146 | 전 주 | 183 SE | 9 | 2 |  | 107 E | 5 | 19 |  | 100 SW | 4 | 26 |  | 120 SW | 7 | 5 |  | 148 SSE | 3 | 25
152 | 울 산 | 133 WSW | 2 | 26 |  | 167 NW | 1 | 19 |  | 127 WSW | 11 | 16 |  | 103 NW | 1 | 3 |  | 127 NE | 10 | 5
155 | 마 산 | [16 empty] | 130 N | 11 | 24
156 | 광 주 | 167 E | 9 | 2 |  | 133 SE | 6 | 13 |  | 167 SSE | 4 | 14 |  | 123 NNW | 3 | 21 |  | 135 SSE | 4 | 3
159 | 부 산 | 230 SW | 6 | 22 |  | 233 SW | 5 | 13 |  | 250 SW | 4 | 28 |  | 163 SW | 6 | 7 |  | 190 SSW | 10 | 13
162 | 통 영 | 200 SSW | 7 | 2 |  | 207 SW | 4 | 2 |  | 227 WSW | 4 | 28 |  | 183 WSW | 9 | 3 |  | 167 WSW | 12 | 30
164 | 무 안
165 | 목 포 | 183 NNW | 10 | 22 |  | 183 NNW | 4 | 8 |  | 193 SW | 4 | 28 |  | 152 NW | 12 | 18 |  | 227 S | 8 | 14
168 | 여 수 | 213 ESE | 7 | 31 |  | 202 NW | 4 | 8 |  | 210 NNE | 9 | 28 |  | 167 NE | 4 | 19 |  | 235 NE | 10 | 5
169 | 흑산도
170 | 완 도 | 110 ESE | 9 | 2 |  | 95 E | 8 | 13 |  | 173 N | 12 | 1 |  | 197 NW | 4 | 5 |  | 178 ESE | 8 | 13
184 | 제 주 | 177 WNW | 2 | 25 |  | 160 NW | 4 | 9 |  | 220 SSW | 4 | 3 |  | 180 NE | 8 | 20 |  | 218 NE | 10 | 5
185 | 제주고층
189 | 서귀포 | 167 SSE | 9 | 2 |  | 120 NE | 9 | 24 |  | 152 NE | 9 | 27 |  | 167 NE | 8 | 20 |  | 187 E | 8 | 9
192 | 진 주 | 130 N | 3 | 15 |  | 133 SSW | 5 | 13 |  | 133 SSW | 4 | 26 |  | 123 S | 9 | 1 |  | 127 S | 8 | 10
201 | 강 화 | 95 W | 1 | 1 |  | 80 WSW | 4 | 16 |  | 95 SW | 4 | 26 |  | 80 SW | 6 | 6 |  | 105 NNW | 8 | 14
202 | 양 평 | 100 WNW | 10 | 23 |  | 110 ENE | 11 | 9 |  | 110 WSW | 4 | 29 |  | 100 WSW | 3 | 25 |  | 90 WNW | 11 | 28
203 | 이 천 | 80 WSW | 10 | 8 |  | 70 SW | 11 | 22 |  | 80 NW | 4 | 29 |  | 70 WNW | 4 | 25 |  | 80 E | 5 | 28
211 | 인 제 | 110 S | 5 | 3 |  | 120 SSE | 5 | 4 |  | 145 SE | 4 | 27 |  | 95 NE | 3 | 30 |  | 105 N | 5 | 28
212 | 홍 천 | 75 SW | 5 | 3 |  | 70 SW | 5 | 4 |  | 95 WSW | 4 | 27 |  | 70 WSW | 10 | 20 |  | 65 WSW | 4 | 28
216 | 태 백 | [16 empty] | 90 NNE | 10 | 5
221 | 제 천 | 90 WNW | 5 | 3 |  | 95 WNW | 5 | 4 |  | 140 W | 4 | 26 |  | 80 WNW | 2 | 1 |  | 75 W | 11 | 28
223 | 충 주 | 70 W | 5 | 11 |  | 70 SW | 5 | 4 |  | 100 SE | 4 | 26 |  | 75 SW | 3 | 25 |  | 70 NE | 4 | 11
226 | 보 은 | 95 WNW | 2 | 26 |  | 95 WSW | 5 | 4 |  | 100 NW | 11 | 30 |  | 100 WNW | 2 | 1 |  | 110 SE | 8 | 14
232 | 천 안 | 90 W | 10 | 22 |  | 95 W | 12 | 11 |  | 115 WNW | 4 | 29 |  | 90 WNW | 10 | 20 |  | 90 WSW | 4 | 26
235 | 보 령 | 110 SSW | 8 | 17 |  | 110 SSW | 8 | 14 |  | 160 SSW | 4 | 26 |  | 140 SE | 4 | 18 |  | 165 S | 8 | 14
236 | 부 여 | 95 NW | 10 | 22 |  | 85 WSW | 12 | 11 |  | 115 SSW | 4 | 26 |  | 100 E | 4 | 18 |  | 110 SE | 8 | 14
238 | 금 산 | 90 W | 3 | 26 |  | 85 SW | 5 | 4 |  | 100 WSW | 4 | 26 |  | 90 S | 4 | 25 |  | 100 SE | 3 | 25
243 | 부 안 | 100 SSE | 9 | 2 |  | 95 NNE | 12 | 5 |  | 110 SW | 4 | 26 |  | 120 NE | 4 | 18 |  | 115 ENE | 4 | 11
244 | 임 실 | 70 SE | 8 | 1 |  | 65 SE | 5 | 5 |  | 70 SSE | 8 | 12 |  | 75 S | 5 | 13 |  | 75 SSE | 5 | 12
245 | 정 읍 | 105 SE | 3 | 24 |  | 70 SSW | 8 | 14 |  | 90 NNE | 8 | 12 |  | 75 SSW | 3 | 20 |  | 80 SE | 5 | 4
247 | 남 원 | 90 NW | 3 | 15 |  | 115 WSW | 12 | 2 |  | 90 WSW | 11 | 16 |  | 85 NW | 2 | 26 |  | 85 SW | 12 | 30
248 | 장 수
256 | 순 천 | 95 WNW | 3 | 26 |  | 80 WNW | 12 | 11 |  | 95 WNW | 3 | 17 |  | 85 WNW | 5 | 1 |  | 90 W | 12 | 30
260 | 장 흥 | 125 NW | 3 | 15 |  | 110 S | 8 | 13 |  | 115 NW | 2 | 18 |  | 95 NW | 2 | 27 |  | 130 SE | 8 | 14
261 | 해 남 | 105 E | 9 | 2 |  | 100 SW | 10 | 19 |  | 110 W | 4 | 28 |  | 90 E | 8 | 20 |  | 110 NE | 10 | 5
262 | 고 흥 | 140 ENE | 7 | 31 |  | 100 ENE | 8 | 13 |  | 80 NE | 6 | 12 |  | 95 S | 8 | 21 |  | 100 NE | 10 | 5
265 | 성산포 | 130 ESE | 9 | 2 |  | 120 NW | 4 | 8 |  | 145 NE | 9 | 27 |  | 145 E | 8 | 21 |  | 245 ESE | 8 | 9
271 | 춘 양
272 | 영 주 | 105 NW | 1 | 11 |  | 135 NW | 12 | 17 |  | 180 NW | 11 | 17 |  | 160 NW | 12 | 18 |  | 175 NW | 1 | 16
273 | 문 경 | 120 W | 3 | 15 |  | 125 SW | 5 | 4 |  | 150 SSW | 4 | 26 |  | 110 SW | 10 | 20 |  | 100 SW | 2 | 20
277 | 영 덕 | 95 NW | 3 | 26 |  | 110 N | 4 | 9 |  | 135 W | 4 | 26 |  | 100 SSE | 6 | 16 |  | 145 N | 10 | 5
278 | 의 성 | 110 NW | 2 | 26 |  | 110 SW | 5 | 4 |  | 115 S | 4 | 26 |  | 105 WNW | 2 | 27 |  | 100 WNW | 12 | 14
279 | 구 미 | 135 WNW | 10 | 22 |  | 130 WNW | 1 | 19 |  | 165 W | 4 | 26 |  | 135 NW | 2 | 8 |  | 130 NW | 2 | 20
281 | 영 천 | 90 NW | 3 | 26 |  | 95 NW | 12 | 22 |  | 100 W | 4 | 29 |  | 100 NW | 12 | 18 |  | 105 NW | 12 | 8
284 | 거 창 | 100 NW | 4 | 24 |  | 95 NW | 2 | 6 |  | 95 W | 4 | 29 |  | 100 W | 2 | 6 |  | 85 NW | 12 | 16
285 | 합 천 | 90 NW | 2 | 25 |  | 80 SSE | 5 | 5 |  | 85 SSW | 4 | 26 |  | 90 SSW | 3 | 29 |  | 100 SSW | 4 | 23
288 | 밀 양 | 110 NNE | 2 | 26 |  | 120 WSW | 10 | 19 |  | 115 WNW | 4 | 29 |  | 110 NNW | 2 | 6 |  | 110 NW | 12 | 30
289 | 산 청 | 150 W | 10 | 8 |  | 105 W | 4 | 8 |  | 90 NW | 4 | 2 |  | 90 NW | 2 | 6 |  | 80 WSW | 12 | 30
294 | 거 제 | 105 NW | 3 | 26 |  | 95 WNW | 11 | 11 |  | 120 W | 4 | 29 |  | 105 SSE | 9 | 3 |  | 105 SSE | 4 | 26
295 | 남 해 | 80 SSW | 6 | 22 |  | 105 SW | 11 | 29 |  | 100 SW | 4 | 26 |  | 115 E | 8 | 21 |  | 130 S | 8 | 14
지 점 |  | 1976 년 |  |  |  | 1977 년 |  |  |  | 1978 년 |  |  |  | 1979 년 |  |  |  | 1980 년
번 호 | 지 명 | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일
90 | 속 초 | 167 W | 11 | 26 |  | 150 WSW | 11 | 19 |  | 250 WSW | 4 | 8 |  | 267 WSW | 2 | 10 |  | 267 SSW | 4 | 19
95 | 철 원
98 | 동두천
99 | 문 산
100 | 대관령 | 135 W | 4 | 23 |  | 120 W | 2 | 24 |  | 133 WNW | 12 | 7 |  | 178 WNW | 12 | 19 |  | 197 WNW | 10 | 26
101 | 춘 천 | 228 W | 1 | 22 |  | 213 W | 2 | 21 |  | 133 SSW | 4 | 5 |  | 147 W | 11 | 13 |  | 127 WSW | 4 | 1
102 | 백령도
105 | 강 릉 | 153 SW | 1 | 5 |  | 150 SSW | 2 | 25 |  | 167 SSW | 4 | 6 |  | 150 S | 11 | 2 |  | 173 WSW | 10 | 25
106 | 동 해
108 | 서 울 | 153 WNW | 12 | 18 |  | 147 SW | 3 | 24 |  | 152 W | 12 | 1 |  | 173 W | 4 | 13 |  | 177 S | 4 | 19
112 | 인 천 | 177 WNW | 12 | 18 |  | 183 WNW | 3 | 24 |  | 167 WSW | 12 | 1 |  | 162 SE | 12 | 19 |  | 257 WNW | 10 | 25
114 | 원 주 | 110 W | 12 | 18 |  | 120 SW | 3 | 24 |  | 105 W | 12 | 1 |  | 100 W | 4 | 14 |  | 110 W | 5 | 5
115 | 울릉도 | 207 SW | 12 | 18 |  | 267 ENE | 5 | 14 |  | 307 SW | 12 | 1 |  | 233 NNE | 11 | 18 |  | 347 SSW | 10 | 25
119 | 수 원 | 153 NW | 12 | 18 |  | 127 W | 3 | 24 |  | 98 WNW | 4 | 16 |  | 117 NNW | 10 | 20 |  | 117 SW | 4 | 19
121 | 영 월
127 | 충 주 | 140 W | 12 | 18 |  | 140 WSW | 3 | 24 |  | 120 SW | 12 | 1 |  | 100 W | 4 | 16 |  | 95 NW | 1 | 17
129 | 서 산 | 150 W | 12 | 18 |  | 200 WSW | 3 | 24 |  | 135 SW | 12 | 1 |  | 107 W | 1 | 21 |  | 120 S | 4 | 18
130 | 울 진 | 210 W | 1 | 5 |  | 165 N | 5 | 14 |  | 237 NNW | 1 | 9 |  | 230 ESE | 8 | 17 |  | 213 SSW | 4 | 19
131 | 청 주 | 137 S | 1 | 7 |  | 167 WNW | 3 | 24 |  | 147 SSE | 12 | 1 |  | 117 SW | 4 | 23 |  | 170 SW | 4 | 19
133 | 대 전 | 139 WSW | 1 | 4 |  | 140 SW | 3 | 24 |  | 140 SW | 7 | 6 |  | 125 WSW | 3 | 30 |  | 133 WSW | 5 | 5
135 | 추풍령 | 170 W | 4 | 23 |  | 153 W | 5 | 7 |  | 237 W | 2 | 28 |  | 167 W | 11 | 29 |  | 167 W | 1 | 17
136 | 안 동 | 95 WNW | 1 | 22 |  | 85 W | 2 | 15 |  | 75 W | 4 | 6
137 | 상 주
138 | 포 항 | 233 N | 9 | 13 |  | 200 NNE | 8 | 24 |  | 150 NE | 10 | 6 |  | 183 NNE | 9 | 29 |  | 173 SW | 4 | 19
140 | 군 산 | 280 NW | 10 | 28 |  | 217 NW | 4 | 17 |  | 247 WNW | 12 | 1 |  | 270 WNW | 8 | 17 |  | 317 WNW | 10 | 25
143 | 대 구 | 157 W | 10 | 28 |  | 150 W | 4 | 18 |  | 150 NW | 4 | 6 |  | 160 SW | 3 | 30 |  | 167 NNW | 12 | 28
146 | 전 주 | 83 SW | 12 | 8 |  | 87 ESE | 4 | 24 |  | 83 SSE | 6 | 9 |  | 103 SE | 4 | 13 |  | 103 SE | 8 | 13
152 | 울 산 | 207 SW | 6 | 8 |  | 177 NW | 2 | 16 |  | 173 NNW | 4 | 6 |  | 167 N | 11 | 12 |  | 150 NW | 12 | 27
155 | 마 산
156 | 광 주 | 143 NW | 10 | 28 |  | 153 WNW | 4 | 18 |  | 128 NW | 4 | 6 |  | 110 SSE | 4 | 13 |  | 120 WNW | 10 | 25
159 | 부 산 | 227 SSW | 6 | 8 |  | 190 SSW | 4 | 15 |  | 183 SSW | 8 | 20 |  | 233 SSW | 8 | 17 |  | 245 SSW | 4 | 6
162 | 통 영 | 240 SW | 6 | 8 |  | 200 SSW | 11 | 21 |  | 200 S | 8 | 20 |  | 235 SE | 8 | 17 |  | 300 SSW | 4 | 6
165 | 목 포 | 197 NNW | 12 | 8 |  | 183 NNW | 2 | 21 |  | 197 NNW | 12 | 19 |  | 210 S | 8 | 17 |  | 237 NNW | 10 | 25
168 | 여 수 | 190 NE | 9 | 11 |  | 152 NE | 8 | 24 |  | 233 ENE | 6 | 20 |  | 203 S | 8 | 17 |  | 202 NE | 11 | 21
169 | 흑산도
170 | 완 도 | 95 | 3 | 16 |  | 90 NE | 8 | 23 |  | 115 ESE | 8 | 20 |  | 145 S | 8 | 17 |  | 100 E | 8 | 13
175 | 진 도
184 | 제 주 | 233 WNW | 12 | 8 |  | 237 SSW | 4 | 24 |  | 203 ENE | 9 | 15 |  | 177 WSW | 3 | 30 |  | 233 SSW | 4 | 6
185 | 고 산
189 | 서귀포 | 185 NNE | 7 | 19 |  | 183 NE | 8 | 23 |  | 190 SSE | 8 | 20 |  | 233 SSE | 8 | 17 |  | 183 S | 8 | 13
192 | 진 주 | 127 W | 5 | 5 |  | 163 WSW | 4 | 18 |  | 118 NW | 4 | 6 |  | 133 W | 5 | 11 |  | 133 WNW | 5 | 5
201 | 강 화 | 110 WNW | 12 | 18 |  | 100 S | 3 | 24 |  | 95 WNW | 12 | 1 |  | 100 WNW | 4 | 13 |  | 155 S | 4 | 19
202 | 양 평 | 125 WNW | 12 | 18 |  | 115 SW | 3 | 24 |  | 100 SSW | 4 | 5 |  | 90 SSW | 4 | 16 |  | 110 ESE | 10 | 16
203 | 이 천 | 90 W | 12 | 18 |  | 105 W | 3 | 24 |  | 75 NNE | 10 | 27 |  | 75 W | 4 | 14 |  | 95 NW | 4 | 19
211 | 인 제 | 115 SW | 4 | 23 |  | 110 S | 4 | 18 |  | 100 ENE | 4 | 15 |  | 110 S | 4 | 14 |  | 115 S | 5 | 27
212 | 홍 천 | 90 WSW | 12 | 18 |  | 85 WSW | 3 | 24 |  | 75 SW | 12 | 1 |  | 75 SW | 4 | 14 |  | 85 WSW | 5 | 5
216 | 태 백
221 | 제 천 | 120 W | 12 | 18 |  | 125 SW | 3 | 24 |  | 115 W | 12 | 1 |  | 110 WNW | 4 | 14 |  | 110 W | 1 | 30
226 | 보 은 | 120 NW | 12 | 8 |  | 105 NW | 2 | 21 |  | 90 NW | 4 | 6 |  | 90 NW | 1 | 18 |  | 105 NNW | 11 | 12
232 | 천 안 | 115 W | 12 | 18 |  | 105 WNW | 2 | 21 |  | 120 NW | 1 | 30 |  | 95 WNW | 4 | 16 |  | 100 SSW | 4 | 19
235 | 보 령 | 135 W | 12 | 8 |  | 115 SE | 4 | 24 |  | 135 SE | 3 | 9 |  | 155 SSE | 4 | 13 |  | 170 SW | 4 | 19
236 | 부 여 | 130 W | 12 | 18 |  | 115 NW | 2 | 21 |  | 100 NW | 4 | 6 |  | 95 E | 8 | 13 |  | 120 SSW | 4 | 19
238 | 금 산 | 120 W | 12 | 8 |  | 110 NE | 2 | 1 |  | 120 NW | 4 | 6 |  | 95 SW | 8 | 17 |  | 95 W | 12 | 28
243 | 부 안 | 100 N | 3 | 19 |  | 100 SSW | 4 | 15 |  | 105 N | 8 | 20 |  | 110 SSW | 4 | 13 |  | 145 SSW | 4 | 18
244 | 임 실 | 95 NE | 12 | 26 |  | 75 SSW | 5 | 1 |  | 95 ENE | 3 | 9 |  | 70 NNE | 5 | 14 |  | 100 SW | 4 | 5
245 | 정 읍 | 95 NW | 12 | 8 |  | 95 ESE | 5 | 21 |  | 80 S | 6 | 9 |  | 110 ESE | 4 | 13 |  | 90 SE | 4 | 5
247 | 남 원 | 115 SW | 12 | 18 |  | 120 NW | 2 | 21 |  | 110 NW | 4 | 6 |  | 100 ENE | 2 | 22 |  | 95 N | 4 | 19
248 | 장 수
256 | 순 천 | 105 NW | 10 | 28 |  | 85 W | 4 | 18 |  | 100 WNW | 6 | 5 |  | 105 SE | 8 | 17 |  | 100 SSW | 10 | 26
260 | 장 흥 | 115 N | 4 | 23 |  | 100 SSE | 6 | 1 |  | 125 SE | 8 | 20 |  | 140 SE | 8 | 17 |  | 100 NW | 12 | 2
261 | 해 남 | 105 SE | 4 | 29 |  | 135 E | 3 | 29 |  | 100 SE | 8 | 20 |  | 125 ESE | 1 | 29 |  | 100 W | 10 | 25
262 | 고 흥 | 95 ENE | 9 | 12 |  | 255 E | 6 | 28 |  | 90 W | 4 | 6 |  | 90 NE | 2 | 22 |  | 90 SW | 12 | 3
265 | 성산포 | 145 NE | 9 | 12 |  | 130 ENE | 3 | 29 |  | 125 NE | 9 | 15 |  | 145 SSW | 8 | 17 |  | 125 NNW | 3 | 9
271 | 봉 화
272 | 영 주 | 165 NW | 12 | 26 |  | 145 NW | 4 | 17 |  | 140 NW | 2 | 23 |  | 120 NW | 1 | 14 |  | 130 NW | 4 | 19
273 | 문 경 | 130 WSW | 4 | 23 |  | 120 W | 2 | 21 |  | 200 NE | 7 | 18 |  | 80 WSW | 4 | 14 |  | 100 W | 12 | 28
277 | 영 덕 | 140 NW | 12 | 18 |  | 160 NNE | 5 | 14 |  | 105 NW | 1 | 21 |  | 125 SSE | 8 | 17 |  | 95 W | 10 | 26
278 | 의 성 | 105 W | 4 | 23 |  | 75 NW | 5 | 7 |  | 95 NW | 7 | 9 |  | 100 W | 4 | 9 |  | 105 W | 2 | 3
279 | 구 미 | 150 WNW | 12 | 8 |  | 170 WNW | 3 | 24 |  | 160 NW | 4 | 6 |  | 140 NW | 4 | 9 |  | 155 WNW | 1 | 30
281 | 영 천 | 95 NW | 12 | 26 |  | 100 NW | 4 | 17 |  | 120 NW | 4 | 6 |  | 125 N | 5 | 17 |  | 150 NW | 1 | 30
284 | 거 창 | 100 WNW | 12 | 18 |  | 115 NW | 3 | 4 |  | 145 WNW | 4 | 6 |  | 120 SE | 8 | 17 |  | 135 NW | 5 | 5
285 | 합 천 | 110 SW | 6 | 8 |  | 85 WSW | 4 | 18 |  | 105 WNW | 4 | 6 |  | 110 SW | 4 | 23 |  | 95 S | 4 | 19
288 | 밀 양 | 115 WNW | 12 | 18 |  | 110 NW | 1 | 27 |  | 120 WNW | 2 | 28 |  | 135 SSE | 8 | 17 |  | 115 NNW | 1 | 30
289 | 산 청 | 95 NW | 1 | 8 |  | 105 NW | 2 | 21 |  | 110 NW | 4 | 6 |  | 100 WNW | 3 | 30 |  | 100 NW | 12 | 26
294 | 거 제 | 140 ESE | 6 | 8 |  | 115 SW | 4 | 20 |  | 125 SSW | 4 | 8 |  | 150 SE | 8 | 17 |  | 130 S | 4 | 19
295 | 남 해 | 100 WNW | 10 | 28 |  | 165 WNW | 12 | 17 |  | 185 SSE | 8 | 20 |  | 185 SW | 4 | 24 |  | 130 SW | 4 | 5
지 점 |  | 1971 년 |  |  |  | 1972 년 |  |  |  | 1973 년 |  |  |  | 1974 년 |  |  |  | 1975 년
번 호 | 지 명 | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일 |  | 값 | 월 | 일
90 | 속 초 | 222 SW | 2 | 17 |  | 210 WSW | 6 | 10 |  | 287 SW | 4 | 18 |  | 217 WSW | 11 | 21 |  | 187 W | 12 | 22
95 | 철 원
98 | 동두천
100 | 대관령 | 120 W | 12 | 17 |  | 135 W | 1 | 21 |  | 150 W | 4 | 18 |  | 135 WNW | 6 | 1 |  | 130 W | 4 | 8
101 | 춘 천 | 130 NNE | 7 | 18 |  | 133 S | 10 | 4 |  | 127 SSE | 4 | 18 |  | 108 SW | 2 | 25 |  | 137 WSW | 11 | 29
105 | 강 릉 | 183 SW | 2 | 17 |  | 183 SSW | 11 | 27 |  | 168 SW | 4 | 18 |  | 233 SSW | 6 | 1 |  | 133 SW | 12 | 30
106 | 동 해
108 | 서 울 | 120 SSW | 3 | 28 |  | 167 WNW | 3 | 31 |  | 170 SW | 8 | 29 |  | 137 WSW | 6 | 1 |  | 117 SW | 9 | 20
112 | 인 천 | 183 NNW | 1 | 4 |  | 228 NW | 3 | 31 |  | 233 S | 8 | 29 |  | 183 NW | 2 | 25 |  | 160 SSW | 7 | 10
114 | 원 주 | 90 NW | 12 | 4 |  | 100 SW | 3 | 16 |  | 105 ESE | 2 | 23 |  | 90 S | 4 | 2 |  | 95 NW | 3 | 30
115 | 울릉도 | 290 NE | 1 | 4 |  | 163 SSW | 10 | 4 |  | 203 SW | 11 | 16 |  | 217 SSW | 4 | 28 |  | 167 E | 12 | 16
119 | 수 원 | 100 WSW | 3 | 2 |  | 100 WNW | 7 | 26 |  | 120 W | 4 | 17 |  | 132 NW | 3 | 22 |  | 130 WNW | 3 | 24
121 | 영 월
129 | 서 산 | 192 S | 8 | 11 |  | 163 S | 11 | 29 |  | 167 S | 8 | 29 |  | 183 SSW | 5 | 31 |  | 170 SW | 9 | 20
130 | 울 진 | 170 W | 12 | 14 |  | 200 WNW | 11 | 30 |  | 210 S | 5 | 7 |  | 210 W | 6 | 1 |  | 175 NNE | 2 | 25
131 | 청 주 | 143 NW | 4 | 9 |  | 233 S | 7 | 26 |  | 167 WSW | 3 | 28 |  | 135 WSW | 4 | 3 |  | 125 N | 11 | 22
133 | 대 전 | 173 SW | 2 | 16 |  | 138 SW | 4 | 28 |  | 150 SW | 11 | 16 |  | 147 SW | 9 | 14 |  | 137 SW | 5 | 4
135 | 추풍령 | 167 W | 2 | 17 |  | 143 W | 5 | 20 |  | 140 W | 4 | 24 |  | 165 W | 2 | 12 |  | 188 W | 3 | 24
136 | 안 동 | [8 empty] | 95 WNW | 11 | 16 |  | 100 NW | 3 | 11 |  | 80 NW | 12 | 22
138 | 포 항 | 193 N | 8 | 5 |  | 180 N | 9 | 14 |  | 167 NE | 1 | 22 |  | 217 N | 7 | 6 |  | 160 N | 11 | 15
140 | 군 산 | 210 WNW | 10 | 11 |  | 317 WNW | 3 | 31 |  | 233 W | 11 | 16 |  | 253 WNW | 12 | 14 |  | 200 ESE | 6 | 23
143 | 대 구 | 160 WSW | 1 | 4 |  | 150 W | 1 | 21 |  | 147 WSW | 11 | 16 |  | 173 W | 3 | 21 |  | 137 NW | 1 | 10
146 | 전 주 | 113 S | 7 | 8 |  | 83 NW | 10 | 4 |  | 98 SE | 8 | 17 |  | 67 E | 2 | 6 |  | 63 SSE | 4 | 26
152 | 울 산 | 147 NW | 11 | 29 |  | 150 NW | 2 | 27 |  | 133 WNW | 12 | 4 |  | 147 WSW | 3 | 21 |  | 170 WNW | 12 | 16
155 | 마 산
156 | 광 주 | 160 NW | 10 | 11 |  | 167 SE | 7 | 26 |  | 147 W | 11 | 19 |  | 123 NNW | 10 | 31 |  | 127 SW | 7 | 16
159 | 부 산 | 207 W | 7 | 8 |  | 227 NW | 12 | 30 |  | 217 SSW | 3 | 27 |  | 250 NW | 10 | 23 |  | 208 NNW | 2 | 8
162 | 통 영 | 228 SSW | 5 | 24 |  | 203 SW | 7 | 4 |  | 183 SSW | 8 | 17 |  | 207 NE | 7 | 6 |  | 223 SW | 4 | 5
164 | 무 안
165 | 목 포 | 300 S | 8 | 10 |  | 260 SE | 7 | 26 |  | 250 SSW | 8 | 17 |  | 182 SSE | 8 | 29 |  | 192 NNW | 2 | 21
168 | 여 수 | 175 NNE | 8 | 5 |  | 233 E | 7 | 26 |  | 172 NNE | 1 | 7 |  | 207 NE | 7 | 6 |  | 162 E | 7 | 30
169 | 흑산도
170 | 완 도 | 75 | 11 | 28 |  | 195 | 7 | 26 |  | 200 | 8 | 17 |  | 125 | 7 | 6 |  | 105 | 4 | 26
184 | 제 주 | 167 NW | 1 | 3 |  | 217 SSE | 7 | 26 |  | 233 SW | 3 | 27 |  | 183 SSW | 4 | 20 |  | 190 SSW | 4 | 5
185 | 제주고층
189 | 서귀포 | 155 S | 8 | 10 |  | 255 ESE | 7 | 26 |  | 220 SE | 8 | 17 |  | 200 NNE | 7 | 6 |  | 167 NE | 10 | 7
192 | 진 주 | 105 SSW | 8 | 10 |  | 133 NW | 3 | 31 |  | 113 WSW | 11 | 16 |  | 100 WSW | 3 | 21 |  | 103 NW | 2 | 21
201 | 강 화 | [8 empty] | 125 W | 11 | 16 |  | 100 WSW | 4 | 21 |  | 90 W | 4 | 8
202 | 양 평 | [8 empty] | 125 NW | 11 | 16 |  | 110 WNW | 4 | 2 |  | 130 SE | 7 | 6
203 | 이 천 | [8 empty] | 115 WSW | 2 | 25 |  | 85 SW | 5 | 14 |  | 75 | 4 | 8
211 | 인 제 | [8 empty] | 100 NW | 8 | 29 |  | 95 NNE | 4 | 7 |  | 137 S | 9 | 20
212 | 홍 천 | [8 empty] | 80 WNW | 4 | 18 |  | 80 WNW | 6 | 1 |  | 70 SE | 4 | 17
216 | 태 백
221 | 제 천 | [8 empty] | 115 WSW | 2 | 6 |  | 110 NW | 3 | 21 |  | 105 WNW | 1 | 18
223 | 충 주 | [8 empty] | 115 WNW | 12 | 21 |  | 110 E | 4 | 7 |  | 95 W | 3 | 30
226 | 보 은 | [8 empty] | 100 N | 12 | 21 |  | 100 NW | 10 | 31 |  | 85 NNW | 2 | 25
232 | 천 안 | [8 empty] | 115 NW | 12 | 21 |  | 120 ESE | 4 | 7 |  | 95 NW | 2 | 20
235 | 보 령 | [8 empty] | 155 S | 5 | 7 |  | 145 SSW | 4 | 3 |  | 160 SE | 6 | 23
236 | 부 여 | [8 empty] | 120 W | 12 | 21 |  | 110 ESE | 4 | 7 |  | 100 SE | 6 | 23
238 | 금 산 | [8 empty] | 110 SW | 4 | 24 |  | 105 SW | 3 | 21 |  | 100 S | 9 | 20
243 | 부 안 | [8 empty] | 120 S | 8 | 17 |  | 125 ENE | 7 | 6 |  | 105 SE | 6 | 23
244 | 임 실 | [8 empty] | 95 | 5 | 7 |  | 95 | 5 | 14 |  | 75 | 2 | 1
245 | 정 읍 | [8 empty] | 100 ESE | 5 | 7 |  | 115 SE | 5 | 13 |  | 85 SE | 6 | 4
247 | 남 원 | [8 empty] | 130 NW | 12 | 21 |  | 90 N | 11 | 21 |  | 95 W | 3 | 31
248 | 장 수
256 | 순 천 | [8 empty] | 105 | 11 | 16 |  | 85 | 3 | 22 |  | 105 W | 4 | 8
260 | 장 흥 | [8 empty] | 165 SE | 8 | 17 |  | 110 | 8 | 29 |  | 130 | 4 | 26
261 | 해 남 | [8 empty] | 130 SE | 8 | 17 |  | 120 E | 7 | 6 |  | 95 ESE | 3 | 5
262 | 고 흥 | [8 empty] | 130 | 8 | 16 |  | 135 | 8 | 29 |  | 85 ENE | 7 | 30
265 | 성산포 | [8 empty] | 165 SSE | 8 | 16 |  | 135 NW | 4 | 21 |  | 145 NW | 2 | 7
271 | 춘 양
272 | 영 주 | [8 empty] | 125 NW | 10 | 21 |  | 155 NW | 2 | 22 |  | 160 WNW | 1 | 11
273 | 문 경 | [8 empty] | 120 W | 12 | 21 |  | 110 W | 2 | 25 |  | 110 SSW | 1 | 12
277 | 영 덕 | [8 empty] | 175 W | 3 | 28 |  | 180 W | 11 | 19 |  | 190 NNE | 4 | 21
278 | 의 성 | [8 empty] | 115 W | 11 | 16 |  | 125 WNW | 3 | 21 |  | 105 SW | 5 | 30
279 | 구 미 | [8 empty] | 165 WNW | 4 | 17 |  | 150 NW | 3 | 11 |  | 140 NW | 1 | 12
281 | 영 천 | [8 empty] | 110 W | 12 | 4 |  | 100 NW | 11 | 18 |  | 100 WNW | 12 | 22
284 | 거 창 | [8 empty] | 120 NW | 4 | 17 |  | 105 NW | 3 | 22 |  | 105 WNW | 3 | 24
285 | 합 천 | [8 empty] | 65 WNW | 12 | 21 |  | 110 SW | 4 | 3 |  | 90 NNW | 3 | 23
288 | 밀 양 | [8 empty] | 160 WNW | 12 | 28 |  | 135 WNW | 3 | 11 |  | 110 NW | 2 | 21
289 | 산 청 | [8 empty] | 100 NW | 12 | 28 |  | 145 NW | 4 | 1 |  | 95 NW | 4 | 8
294 | 거 제 | [8 empty] | 155 SSE | 5 | 7 |  | 145 S | 5 | 14 |  | 145 SSE | 4 | 26
295 | 남 해 | [8 empty] | 110 S | 5 | 7 |  | 125 WNW | 4 | 21 |  | 105 SSW | 4 | 26
|  | 95 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 130 |  | 200

## 요소 spec
번호 | x1 | y1 | x2 | y2 | length (mm) | width (mm) | Area (m^2) | Height (m)
1 | 7502.5 | 0 | 0 | 9000 | 11716.9751 | 130 | 1.5232 | 4.5
2 | 0 | 9000 | 6252.2 | 9000 | 6252.2 | 130 | 0.81279 | 9
3 | 6252.2 | 9000 | 7502.5 | 0 | 9086.4322 | 130 | 1.1812 | 4.5
4 | 0 | 13915 | 6252.2 | 9000 | 7952.8127 | 130 | 1.0339 | 11.4575
5 | 0 | 13915 | 4886.6 | 18830 | 6930.8069 | 130 | 0.901 | 16.3725
6 | 4886.6 | 18830 | 6252.2 | 9000 | 9924.4024 | 130 | 1.2902 | 13.915
7 | 4886.6 | 18830 | 0 | 21030 | 5358.998 | 130 | 0.69667 | 19.93
8 | 0 | 21030 | 3858.6 | 26230 | 6475.2447 | 130 | 0.84178 | 23.63
9 | 3858.6 | 26230 | 4886.6 | 18830 | 7471.0631 | 130 | 0.97124 | 22.53
10 | 3858.6 | 26230 | 0 | 29230 | 4887.6164 | 130 | 0.63539 | 27.73
11 | 0 | 29230 | 3025 | 32230 | 4260.355 | 130 | 0.55385 | 30.73
12 | 3025 | 32230 | 3858.6 | 26230 | 6057.6306 | 130 | 0.78749 | 29.23
13 | 0 | 3442.5 | 3025 | 32230 | 28945.9977 | 110 | 3.1841 | 17.8362
14 | 0 | 3442.5 | 2410.2 | 36655 | 33299.8381 | 110 | 3.663 | 20.0488
15 | 2410.2 | 36655 | 3025 | 32230 | 4467.5053 | 110 | 0.49143 | 34.4425
16 | 0 | 36655 | 2410.2 | 36655 | 2410.2 | 110 | 0.26512 | 36.655
17 | 2410.2 | 36655 | 0 | 39230 | 3526.9943 | 110 | 0.38797 | 37.9425
18 | 2410.2 | 36655 | 2052.5 | 39230 | 2599.7258 | 110 | 0.28597 | 37.9425
19 | 0 | 39230 | 2052.5 | 39230 | 2052.5 | 110 | 0.22578 | 39.23
20 | 2352.5 | 39230 | 0 | 40867.5 | 2866.2977 | 110 | 0.31529 | 40.0487
21 | 2352.5 | 39230 | 1892.68 | 42505 | 3307.1225 | 110 | 0.36378 | 40.8675
22 | 0 | 40867.5 | 1892.68 | 42505 | 2502.7273 | 110 | 0.2753 | 41.6863
23 | 1892.68 | 42505 | 0 | 44130 | 2494.5666 | 80 | 0.19957 | 43.3175
24 | 1892.68 | 42505 | 1734.1 | 45755 | 3253.8666 | 80 | 0.26031 | 44.13
25 | 0 | 44130 | 1734.1 | 45755 | 2376.4949 | 80 | 0.19012 | 44.9425
26 | 1734.1 | 45755 | 0 | 45755 | 1734.1 | 80 | 0.13873 | 45.755
27 | 1734.1 | 45755 | 0 | 48330 | 3104.469 | 80 | 0.24836 | 47.0425
28 | 1734.1 | 45755 | 1608.42 | 48330 | 2578.0653 | 80 | 0.20625 | 47.0425
29 | 0 | 48330 | 1608.42 | 48330 | 1608.42 | 90 | 0.14476 | 48.33
30 | 0 | 51592.5 | 1608.42 | 48330 | 3637.4333 | 90 | 0.32737 | 49.9612
31 | 1608.42 | 48330 | 1502.28 | 50505 | 2177.5883 | 90 | 0.19598 | 49.4175
32 | 1502.28 | 50505 | 0 | 51592.5 | 1854.5893 | 90 | 0.16691 | 51.0487
33 | 0 | 52445 | 1502.28 | 50505 | 2453.6596 | 90 | 0.22083 | 51.475
34 | 0 | 52445 | 1396.14 | 52680 | 1415.7796 | 90 | 0.12742 | 52.5625
35 | 1502.28 | 50505 | 1396.14 | 52680 | 2177.5883 | 90 | 0.19598 | 51.5925
36 | 0 | 51897.5 | 1396.14 | 52680 | 1600.4728 | 90 | 0.14404 | 52.2888
37 | 1396.14 | 52680 | 1290 | 54885 | 2207.5531 | 90 | 0.19868 | 53.7825
38 | 0 | 51897.5 | 1290 | 54885 | 3254.1137 | 90 | 0.29287 | 53.3912
39 | 0 | 54885 | 1290 | 54885 | 1290 | 60 | 0.0774 | 54.885
40 | 1290 | 54885 | 0 | 57460 | 2880.0564 | 60 | 0.1728 | 56.1725
41 | 1290 | 54885 | 3198.5 | 57460 | 3205.1517 | 60 | 0.19231 | 56.1725
42 | 0 | 57460 | 3198.5 | 57460 | 3198.5 | 60 | 0.19191 | 57.46
43 | 4440 | 59135 | 0 | 57460 | 4745.4426 | 60 | 0.28473 | 58.2975
44 | 3198.5 | 57460 | 11971 | 54885 | 9142.6135 | 60 | 0.54856 | 56.1725
45 | 1290 | 54885 | 11971 | 54885 | 10681 | 60 | 0.64086 | 54.885
46 | 1608.42 | 48330 | 12783.1 | 45755 | 11467.5236 | 80 | 0.9174 | 47.0425
47 | 1734.1 | 45755 | 12783.1 | 45755 | 11049 | 80 | 0.88392 | 45.755
48 | 2052.5 | 39230 | 13838.2 | 36655 | 12063.7204 | 110 | 1.327 | 37.9425
49 | 2410.2 | 36655 | 13838.2 | 36655 | 11428 | 110 | 1.2571 | 36.655
[6 empty] | Af | 30.4385 | m^2